## Лист1
# | Var.Name | Var.Visual | Var.Type | ID | R/W
1 | GLOBALS.Focus | DT_NUMERIC | MB1 | 40002 | R | 41 | Modbusparam{1, | 40002,/"40002_GLOBALS.Focus | Modbusparam{1,40002,/"40002_GLOBALS.Focus/", | /"DT_NUMERIC/", | Modbusparam{1,40002,/"40002_GLOBALS.Focus/",/"DT_NUMERIC/",},
2 | GLOBALS.Program | DT_NUMERIC | MB3 | 40004 | R |  | Modbusparam{2, | 40004,/"40004_GLOBALS.Program | Modbusparam{2,40004,/"40004_GLOBALS.Program/", | /"DT_NUMERIC/", | Modbusparam{2,40004,/"40004_GLOBALS.Program/",/"DT_NUMERIC/",},
3 | GLOBALS.Year | DT_NUMERIC | MB210 | 40035 | R |  | Modbusparam{3, | 40035,/"40035_GLOBALS.Year | Modbusparam{3,40035,/"40035_GLOBALS.Year/", | /"DT_NUMERIC/", | Modbusparam{3,40035,/"40035_GLOBALS.Year/",/"DT_NUMERIC/",},
4 | GLOBALS.Month | DT_NUMERIC | MB211 | 40036 | R |  | Modbusparam{4, | 40036,/"40036_GLOBALS.Month | Modbusparam{4,40036,/"40036_GLOBALS.Month/", | /"DT_NUMERIC/", | Modbusparam{4,40036,/"40036_GLOBALS.Month/",/"DT_NUMERIC/",},
5 | GLOBALS.Day | DT_NUMERIC | MB212 | 40037 | R |  | Modbusparam{5, | 40037,/"40037_GLOBALS.Day | Modbusparam{5,40037,/"40037_GLOBALS.Day/", | /"DT_NUMERIC/", | Modbusparam{5,40037,/"40037_GLOBALS.Day/",/"DT_NUMERIC/",},
6 | GLOBALS.Hour | DT_NUMERIC | MB213 | 40038 | R |  | Modbusparam{6, | 40038,/"40038_GLOBALS.Hour | Modbusparam{6,40038,/"40038_GLOBALS.Hour/", | /"DT_NUMERIC/", | Modbusparam{6,40038,/"40038_GLOBALS.Hour/",/"DT_NUMERIC/",},
7 | GLOBALS.Minute | DT_NUMERIC | MB214 | 40039 | R |  | Modbusparam{7, | 40039,/"40039_GLOBALS.Minute | Modbusparam{7,40039,/"40039_GLOBALS.Minute/", | /"DT_NUMERIC/", | Modbusparam{7,40039,/"40039_GLOBALS.Minute/",/"DT_NUMERIC/",},
8 | GLOBALS.Second | DT_NUMERIC | MB215 | 40040 | R |  | Modbusparam{8, | 40040,/"40040_GLOBALS.Second | Modbusparam{8,40040,/"40040_GLOBALS.Second/", | /"DT_NUMERIC/", | Modbusparam{8,40040,/"40040_GLOBALS.Second/",/"DT_NUMERIC/",},
9 | GLOBALS.Day_of_the_week | DT_NUMERIC | MB216 | 40042 | R |  | Modbusparam{9, | 40042,/"40042_GLOBALS.Day_of_the_week | Modbusparam{9,40042,/"40042_GLOBALS.Day_of_the_week/", | /"DT_NUMERIC/", | Modbusparam{9,40042,/"40042_GLOBALS.Day_of_the_week/",/"DT_NUMERIC/",},
10 | GLOBALS.Modem_Status | DT_NUMERIC | MB218 | 40043 | R |  | Modbusparam{10, | 40043,/"40043_GLOBALS.Modem_Status | Modbusparam{10,40043,/"40043_GLOBALS.Modem_Status/", | /"DT_NUMERIC/", | Modbusparam{10,40043,/"40043_GLOBALS.Modem_Status/",/"DT_NUMERIC/",},
106 | RID1000A_BOARD.COM_protocol | DT_SERIAL_PROTOCOLS_RID | MB250 | 40050 | R | 58 | Modbusparam{106, | 40050,/"40050_RID1000A_BOARD.COM_protocol | Modbusparam{106,40050,/"40050_RID1000A_BOARD.COM_protocol/", | /"DT_SERIAL_PROTOCOLS_RID/", | Modbusparam{106,40050,/"40050_RID1000A_BOARD.COM_protocol/",/"DT_SERIAL_PROTOCOLS_RID/",},
107 | RID1000A_BOARD.Baud_rate_COM | DT_SERIAL_BAUDRATE | MB251 | 40051 | R |  | Modbusparam{107, | 40051,/"40051_RID1000A_BOARD.Baud_rate_COM | Modbusparam{107,40051,/"40051_RID1000A_BOARD.Baud_rate_COM/", | /"DT_SERIAL_BAUDRATE/", | Modbusparam{107,40051,/"40051_RID1000A_BOARD.Baud_rate_COM/",/"DT_SERIAL_BAUDRATE/",},
108 | RID1000A_BOARD.RS485_protocol | DT_SERIAL_PROTOCOLS_RID | MB255 | 40055 | R |  | Modbusparam{108, | 40055,/"40055_RID1000A_BOARD.RS485_protocol | Modbusparam{108,40055,/"40055_RID1000A_BOARD.RS485_protocol/", | /"DT_SERIAL_PROTOCOLS_RID/", | Modbusparam{108,40055,/"40055_RID1000A_BOARD.RS485_protocol/",/"DT_SERIAL_PROTOCOLS_RID/",},
109 | RID1000A_BOARD.Baud_rate_RS485 | DT_SERIAL_BAUDRATE | MB256 | 40056 | R |  | Modbusparam{109, | 40056,/"40056_RID1000A_BOARD.Baud_rate_RS485 | Modbusparam{109,40056,/"40056_RID1000A_BOARD.Baud_rate_RS485/", | /"DT_SERIAL_BAUDRATE/", | Modbusparam{109,40056,/"40056_RID1000A_BOARD.Baud_rate_RS485/",/"DT_SERIAL_BAUDRATE/",},
110 | RID1000A_BOARD.Bit_rates | DT_CAN_BITRATES | MB267 | 40060 | R |  | Modbusparam{110, | 40060,/"40060_RID1000A_BOARD.Bit_rates | Modbusparam{110,40060,/"40060_RID1000A_BOARD.Bit_rates/", | /"DT_CAN_BITRATES/", | Modbusparam{110,40060,/"40060_RID1000A_BOARD.Bit_rates/",/"DT_CAN_BITRATES/",},
111 | RID1000A_BOARD.CAN_protocol | DT_CAN_PROTOCOLS | MB268 | 40061 | R |  | Modbusparam{111, | 40061,/"40061_RID1000A_BOARD.CAN_protocol | Modbusparam{111,40061,/"40061_RID1000A_BOARD.CAN_protocol/", | /"DT_CAN_PROTOCOLS/", | Modbusparam{111,40061,/"40061_RID1000A_BOARD.CAN_protocol/",/"DT_CAN_PROTOCOLS/",},
112 | RID1000A_BOARD.Address | DT_NUMERIC | MB260 | 40062 | R |  | Modbusparam{112, | 40062,/"40062_RID1000A_BOARD.Address | Modbusparam{112,40062,/"40062_RID1000A_BOARD.Address/", | /"DT_NUMERIC/", | Modbusparam{112,40062,/"40062_RID1000A_BOARD.Address/",/"DT_NUMERIC/",},
113 | RID1000A_BOARD.Centre_SMS | DT_STRING | MW270 | 40063 | R |  | Modbusparam{113, | 40063,/"40063_RID1000A_BOARD.Centre_SMS | Modbusparam{113,40063,/"40063_RID1000A_BOARD.Centre_SMS/", | /"DT_STRING/", | Modbusparam{113,40063,/"40063_RID1000A_BOARD.Centre_SMS/",/"DT_STRING/",},
114 | RID1000A_BOARD.SMS_1_number | DT_STRING | MW272 | 40064 | R |  | Modbusparam{114, | 40064,/"40064_RID1000A_BOARD.SMS_1_number | Modbusparam{114,40064,/"40064_RID1000A_BOARD.SMS_1_number/", | /"DT_STRING/", | Modbusparam{114,40064,/"40064_RID1000A_BOARD.SMS_1_number/",/"DT_STRING/",},
115 | RID1000A_BOARD.SMS_2_number | DT_STRING | MW274 | 40065 | R |  | Modbusparam{115, | 40065,/"40065_RID1000A_BOARD.SMS_2_number | Modbusparam{115,40065,/"40065_RID1000A_BOARD.SMS_2_number/", | /"DT_STRING/", | Modbusparam{115,40065,/"40065_RID1000A_BOARD.SMS_2_number/",/"DT_STRING/",},
116 | RID1000A_BOARD.SMS_3_number | DT_STRING | MW276 | 40066 | R |  | Modbusparam{116, | 40066,/"40066_RID1000A_BOARD.SMS_3_number | Modbusparam{116,40066,/"40066_RID1000A_BOARD.SMS_3_number/", | /"DT_STRING/", | Modbusparam{116,40066,/"40066_RID1000A_BOARD.SMS_3_number/",/"DT_STRING/",},
117 | RID1000A_BOARD.SMS_4_number | DT_STRING | MW278 | 40067 | R |  | Modbusparam{117, | 40067,/"40067_RID1000A_BOARD.SMS_4_number | Modbusparam{117,40067,/"40067_RID1000A_BOARD.SMS_4_number/", | /"DT_STRING/", | Modbusparam{117,40067,/"40067_RID1000A_BOARD.SMS_4_number/",/"DT_STRING/",},
118 | RID1000A_BOARD.SMS_5_number | DT_STRING | MW280 | 40068 | R |  | Modbusparam{118, | 40068,/"40068_RID1000A_BOARD.SMS_5_number | Modbusparam{118,40068,/"40068_RID1000A_BOARD.SMS_5_number/", | /"DT_STRING/", | Modbusparam{118,40068,/"40068_RID1000A_BOARD.SMS_5_number/",/"DT_STRING/",},
119 | RID1000A_BOARD.Sampling_time | DT_NUMERIC | MW430 | 40069 | R |  | Modbusparam{119, | 40069,/"40069_RID1000A_BOARD.Sampling_time | Modbusparam{119,40069,/"40069_RID1000A_BOARD.Sampling_time/", | /"DT_NUMERIC/", | Modbusparam{119,40069,/"40069_RID1000A_BOARD.Sampling_time/",/"DT_NUMERIC/",},
120 | RID1000A_BOARD.Datalogger_Enable | DT_NUMERIC_OFF | M432.1 | 40071 | R |  | Modbusparam{120, | 40071,/"40071_RID1000A_BOARD.Datalogger_Enable | Modbusparam{120,40071,/"40071_RID1000A_BOARD.Datalogger_Enable/", | /"DT_NUMERIC_OFF/", | Modbusparam{120,40071,/"40071_RID1000A_BOARD.Datalogger_Enable/",/"DT_NUMERIC_OFF/",},
121 | RID1000A_BOARD.Upload_data_SMS | DT_STRING | MW586 | 40077 | R |  | Modbusparam{121, | 40077,/"40077_RID1000A_BOARD.Upload_data_SMS | Modbusparam{121,40077,/"40077_RID1000A_BOARD.Upload_data_SMS/", | /"DT_STRING/", | Modbusparam{121,40077,/"40077_RID1000A_BOARD.Upload_data_SMS/",/"DT_STRING/",},
122 | RID1000A_BOARD.Upload_adta_apn | DT_STRING | MW588 | 40078 | R |  | Modbusparam{122, | 40078,/"40078_RID1000A_BOARD.Upload_adta_apn | Modbusparam{122,40078,/"40078_RID1000A_BOARD.Upload_adta_apn/", | /"DT_STRING/", | Modbusparam{122,40078,/"40078_RID1000A_BOARD.Upload_adta_apn/",/"DT_STRING/",},
123 | RID1000A_BOARD.Upload_data_server | DT_STRING | MW590 | 40079 | R |  | Modbusparam{123, | 40079,/"40079_RID1000A_BOARD.Upload_data_server | Modbusparam{123,40079,/"40079_RID1000A_BOARD.Upload_data_server/", | /"DT_STRING/", | Modbusparam{123,40079,/"40079_RID1000A_BOARD.Upload_data_server/",/"DT_STRING/",},
124 | RID1000A_BOARD.Upload_data_service | DT_STRING | MW592 | 40080 | R |  | Modbusparam{124, | 40080,/"40080_RID1000A_BOARD.Upload_data_service | Modbusparam{124,40080,/"40080_RID1000A_BOARD.Upload_data_service/", | /"DT_STRING/", | Modbusparam{124,40080,/"40080_RID1000A_BOARD.Upload_data_service/",/"DT_STRING/",},
125 | RID1000A_BOARD.Server_port | DT_NUMERIC | MW594 | 40081 | R |  | Modbusparam{125, | 40081,/"40081_RID1000A_BOARD.Server_port | Modbusparam{125,40081,/"40081_RID1000A_BOARD.Server_port/", | /"DT_NUMERIC/", | Modbusparam{125,40081,/"40081_RID1000A_BOARD.Server_port/",/"DT_NUMERIC/",},
126 | RID1000A_BOARD.Upload_interval | DT_NUMERIC | MW596 | 40082 | R |  | Modbusparam{126, | 40082,/"40082_RID1000A_BOARD.Upload_interval | Modbusparam{126,40082,/"40082_RID1000A_BOARD.Upload_interval/", | /"DT_NUMERIC/", | Modbusparam{126,40082,/"40082_RID1000A_BOARD.Upload_interval/",/"DT_NUMERIC/",},
127 | RID1000A_BOARD.Upload_type | DT_UPLOAD_TYPE | MB598 | 40083 | R |  | Modbusparam{127, | 40083,/"40083_RID1000A_BOARD.Upload_type | Modbusparam{127,40083,/"40083_RID1000A_BOARD.Upload_type/", | /"DT_UPLOAD_TYPE/", | Modbusparam{127,40083,/"40083_RID1000A_BOARD.Upload_type/",/"DT_UPLOAD_TYPE/",},
128 | RID1000A_BOARD.ID_Upload | DT_NUMERIC_OFF | MW146 | 40084 | R |  | Modbusparam{128, | 40084,/"40084_RID1000A_BOARD.ID_Upload | Modbusparam{128,40084,/"40084_RID1000A_BOARD.ID_Upload/", | /"DT_NUMERIC_OFF/", | Modbusparam{128,40084,/"40084_RID1000A_BOARD.ID_Upload/",/"DT_NUMERIC_OFF/",},
129 | RID1000A_BOARD.Input_type_1 | DT_DIO_TYPES | MB535 | 40085 | R |  | Modbusparam{129, | 40085,/"40085_RID1000A_BOARD.Input_type_1 | Modbusparam{129,40085,/"40085_RID1000A_BOARD.Input_type_1/", | /"DT_DIO_TYPES/", | Modbusparam{129,40085,/"40085_RID1000A_BOARD.Input_type_1/",/"DT_DIO_TYPES/",},
130 | RID1000A_BOARD.Input_type_2 | DT_DIO_TYPES | MB536 | 40086 | R |  | Modbusparam{130, | 40086,/"40086_RID1000A_BOARD.Input_type_2 | Modbusparam{130,40086,/"40086_RID1000A_BOARD.Input_type_2/", | /"DT_DIO_TYPES/", | Modbusparam{130,40086,/"40086_RID1000A_BOARD.Input_type_2/",/"DT_DIO_TYPES/",},
131 | RID1000A_BOARD.Input_type_3 | DT_DIO_TYPES | MB537 | 40087 | R |  | Modbusparam{131, | 40087,/"40087_RID1000A_BOARD.Input_type_3 | Modbusparam{131,40087,/"40087_RID1000A_BOARD.Input_type_3/", | /"DT_DIO_TYPES/", | Modbusparam{131,40087,/"40087_RID1000A_BOARD.Input_type_3/",/"DT_DIO_TYPES/",},
132 | RID1000A_BOARD.Input_type_4 | DT_DIO_TYPES | MB538 | 40088 | R |  | Modbusparam{132, | 40088,/"40088_RID1000A_BOARD.Input_type_4 | Modbusparam{132,40088,/"40088_RID1000A_BOARD.Input_type_4/", | /"DT_DIO_TYPES/", | Modbusparam{132,40088,/"40088_RID1000A_BOARD.Input_type_4/",/"DT_DIO_TYPES/",},
133 | RID1000A_BOARD.Input_type_5 | DT_DIO_TYPES | MB539 | 40089 | R |  | Modbusparam{133, | 40089,/"40089_RID1000A_BOARD.Input_type_5 | Modbusparam{133,40089,/"40089_RID1000A_BOARD.Input_type_5/", | /"DT_DIO_TYPES/", | Modbusparam{133,40089,/"40089_RID1000A_BOARD.Input_type_5/",/"DT_DIO_TYPES/",},
134 | RID1000A_BOARD.Emergency_input_type | DT_DIO_TYPES | MB585 | 40090 | R |  | Modbusparam{134, | 40090,/"40090_RID1000A_BOARD.Emergency_input_type | Modbusparam{134,40090,/"40090_RID1000A_BOARD.Emergency_input_type/", | /"DT_DIO_TYPES/", | Modbusparam{134,40090,/"40090_RID1000A_BOARD.Emergency_input_type/",/"DT_DIO_TYPES/",},
135 | RID1000A_BOARD.Output_type_EV | DT_DIO_TYPES | MB540 | 40091 | R |  | Modbusparam{135, | 40091,/"40091_RID1000A_BOARD.Output_type_EV | Modbusparam{135,40091,/"40091_RID1000A_BOARD.Output_type_EV/", | /"DT_DIO_TYPES/", | Modbusparam{135,40091,/"40091_RID1000A_BOARD.Output_type_EV/",/"DT_DIO_TYPES/",},
136 | RID1000A_BOARD.Output_type_AVV | DT_DIO_TYPES | MB541 | 40092 | R |  | Modbusparam{136, | 40092,/"40092_RID1000A_BOARD.Output_type_AVV | Modbusparam{136,40092,/"40092_RID1000A_BOARD.Output_type_AVV/", | /"DT_DIO_TYPES/", | Modbusparam{136,40092,/"40092_RID1000A_BOARD.Output_type_AVV/",/"DT_DIO_TYPES/",},
137 | RID1000A_BOARD.Output_type_1 | DT_DIO_TYPES | MB542 | 40093 | R |  | Modbusparam{137, | 40093,/"40093_RID1000A_BOARD.Output_type_1 | Modbusparam{137,40093,/"40093_RID1000A_BOARD.Output_type_1/", | /"DT_DIO_TYPES/", | Modbusparam{137,40093,/"40093_RID1000A_BOARD.Output_type_1/",/"DT_DIO_TYPES/",},
138 | RID1000A_BOARD.Output_type_2 | DT_DIO_TYPES | MB543 | 40094 | R |  | Modbusparam{138, | 40094,/"40094_RID1000A_BOARD.Output_type_2 | Modbusparam{138,40094,/"40094_RID1000A_BOARD.Output_type_2/", | /"DT_DIO_TYPES/", | Modbusparam{138,40094,/"40094_RID1000A_BOARD.Output_type_2/",/"DT_DIO_TYPES/",},
139 | RID1000A_BOARD.Output_type_3 | DT_DIO_TYPES | MB544 | 40095 | R |  | Modbusparam{139, | 40095,/"40095_RID1000A_BOARD.Output_type_3 | Modbusparam{139,40095,/"40095_RID1000A_BOARD.Output_type_3/", | /"DT_DIO_TYPES/", | Modbusparam{139,40095,/"40095_RID1000A_BOARD.Output_type_3/",/"DT_DIO_TYPES/",},
140 | RID1000A_BOARD.Output_type_4 | DT_DIO_TYPES | MB545 | 40096 | R |  | Modbusparam{140, | 40096,/"40096_RID1000A_BOARD.Output_type_4 | Modbusparam{140,40096,/"40096_RID1000A_BOARD.Output_type_4/", | /"DT_DIO_TYPES/", | Modbusparam{140,40096,/"40096_RID1000A_BOARD.Output_type_4/",/"DT_DIO_TYPES/",},
141 | RID1000A_BOARD.Analog_type_1 | DT_ANI_TYPES | MB546 | 40097 | R |  | Modbusparam{141, | 40097,/"40097_RID1000A_BOARD.Analog_type_1 | Modbusparam{141,40097,/"40097_RID1000A_BOARD.Analog_type_1/", | /"DT_ANI_TYPES/", | Modbusparam{141,40097,/"40097_RID1000A_BOARD.Analog_type_1/",/"DT_ANI_TYPES/",},
142 | RID1000A_BOARD.Analog_type_2 | DT_ANI_TYPES | MB547 | 40098 | R |  | Modbusparam{142, | 40098,/"40098_RID1000A_BOARD.Analog_type_2 | Modbusparam{142,40098,/"40098_RID1000A_BOARD.Analog_type_2/", | /"DT_ANI_TYPES/", | Modbusparam{142,40098,/"40098_RID1000A_BOARD.Analog_type_2/",/"DT_ANI_TYPES/",},
143 | RID1000A_BOARD.Analog_type_3 | DT_ANI_TYPES | MB548 | 40099 | R |  | Modbusparam{143, | 40099,/"40099_RID1000A_BOARD.Analog_type_3 | Modbusparam{143,40099,/"40099_RID1000A_BOARD.Analog_type_3/", | /"DT_ANI_TYPES/", | Modbusparam{143,40099,/"40099_RID1000A_BOARD.Analog_type_3/",/"DT_ANI_TYPES/",},
144 | RID1000A_BOARD.Offset_VRR | DT_NUMERIC | MR549 | 40100 | R |  | Modbusparam{144, | 40100,/"40100_RID1000A_BOARD.Offset_VRR | Modbusparam{144,40100,/"40100_RID1000A_BOARD.Offset_VRR/", | /"DT_NUMERIC/", | Modbusparam{144,40100,/"40100_RID1000A_BOARD.Offset_VRR/",/"DT_NUMERIC/",},
145 | RID1000A_BOARD.Offset_VRS | DT_NUMERIC | MR553 | 40101 | R |  | Modbusparam{145, | 40101,/"40101_RID1000A_BOARD.Offset_VRS | Modbusparam{145,40101,/"40101_RID1000A_BOARD.Offset_VRS/", | /"DT_NUMERIC/", | Modbusparam{145,40101,/"40101_RID1000A_BOARD.Offset_VRS/",/"DT_NUMERIC/",},
146 | RID1000A_BOARD.Offset_VRT | DT_NUMERIC | MR557 | 40102 | R |  | Modbusparam{146, | 40102,/"40102_RID1000A_BOARD.Offset_VRT | Modbusparam{146,40102,/"40102_RID1000A_BOARD.Offset_VRT/", | /"DT_NUMERIC/", | Modbusparam{146,40102,/"40102_RID1000A_BOARD.Offset_VRT/",/"DT_NUMERIC/",},
147 | RID1000A_BOARD.Offset_VGR | DT_NUMERIC | MR561 | 40103 | R |  | Modbusparam{147, | 40103,/"40103_RID1000A_BOARD.Offset_VGR | Modbusparam{147,40103,/"40103_RID1000A_BOARD.Offset_VGR/", | /"DT_NUMERIC/", | Modbusparam{147,40103,/"40103_RID1000A_BOARD.Offset_VGR/",/"DT_NUMERIC/",},
148 | RID1000A_BOARD.Offset_VGS | DT_NUMERIC | MR565 | 40104 | R |  | Modbusparam{148, | 40104,/"40104_RID1000A_BOARD.Offset_VGS | Modbusparam{148,40104,/"40104_RID1000A_BOARD.Offset_VGS/", | /"DT_NUMERIC/", | Modbusparam{148,40104,/"40104_RID1000A_BOARD.Offset_VGS/",/"DT_NUMERIC/",},
149 | RID1000A_BOARD.Offset_VGT | DT_NUMERIC | MR569 | 40105 | R |  | Modbusparam{149, | 40105,/"40105_RID1000A_BOARD.Offset_VGT | Modbusparam{149,40105,/"40105_RID1000A_BOARD.Offset_VGT/", | /"DT_NUMERIC/", | Modbusparam{149,40105,/"40105_RID1000A_BOARD.Offset_VGT/",/"DT_NUMERIC/",},
150 | RID1000A_BOARD.Offset_IR | DT_REAL_1 | MR573 | 40106 | R |  | Modbusparam{150, | 40106,/"40106_RID1000A_BOARD.Offset_IR | Modbusparam{150,40106,/"40106_RID1000A_BOARD.Offset_IR/", | /"DT_REAL_1/", | Modbusparam{150,40106,/"40106_RID1000A_BOARD.Offset_IR/",/"DT_REAL_1/",},
151 | RID1000A_BOARD.Offset_IS | DT_REAL_1 | MR577 | 40107 | R |  | Modbusparam{151, | 40107,/"40107_RID1000A_BOARD.Offset_IS | Modbusparam{151,40107,/"40107_RID1000A_BOARD.Offset_IS/", | /"DT_REAL_1/", | Modbusparam{151,40107,/"40107_RID1000A_BOARD.Offset_IS/",/"DT_REAL_1/",},
152 | RID1000A_BOARD.Offset_IT | DT_REAL_1 | MR581 | 40108 | R |  | Modbusparam{152, | 40108,/"40108_RID1000A_BOARD.Offset_IT | Modbusparam{152,40108,/"40108_RID1000A_BOARD.Offset_IT/", | /"DT_REAL_1/", | Modbusparam{152,40108,/"40108_RID1000A_BOARD.Offset_IT/",/"DT_REAL_1/",},
11 | RID1000A_BOARD.Input_J4.8 | DT_ONOFF | I0.0 | 40134 | R | 102 | Modbusparam{11, | 40134,/"40134_RID1000A_BOARD.Input_J4.8 | Modbusparam{11,40134,/"40134_RID1000A_BOARD.Input_J4.8/", | /"DT_ONOFF/", | Modbusparam{11,40134,/"40134_RID1000A_BOARD.Input_J4.8/",/"DT_ONOFF/",},
12 | RID1000A_BOARD.Input_J4.7 | DT_ONOFF | I0.1 | 40135 | R |  | Modbusparam{12, | 40135,/"40135_RID1000A_BOARD.Input_J4.7 | Modbusparam{12,40135,/"40135_RID1000A_BOARD.Input_J4.7/", | /"DT_ONOFF/", | Modbusparam{12,40135,/"40135_RID1000A_BOARD.Input_J4.7/",/"DT_ONOFF/",},
13 | RID1000A_BOARD.Input_J4.6 | DT_ONOFF | I0.2 | 40136 | R |  | Modbusparam{13, | 40136,/"40136_RID1000A_BOARD.Input_J4.6 | Modbusparam{13,40136,/"40136_RID1000A_BOARD.Input_J4.6/", | /"DT_ONOFF/", | Modbusparam{13,40136,/"40136_RID1000A_BOARD.Input_J4.6/",/"DT_ONOFF/",},
14 | RID1000A_BOARD.Input_J4.5 | DT_ONOFF | I0.3 | 40137 | R |  | Modbusparam{14, | 40137,/"40137_RID1000A_BOARD.Input_J4.5 | Modbusparam{14,40137,/"40137_RID1000A_BOARD.Input_J4.5/", | /"DT_ONOFF/", | Modbusparam{14,40137,/"40137_RID1000A_BOARD.Input_J4.5/",/"DT_ONOFF/",},
15 | RID1000A_BOARD.Input_J4.4 | DT_ONOFF | I0.4 | 40138 | R |  | Modbusparam{15, | 40138,/"40138_RID1000A_BOARD.Input_J4.4 | Modbusparam{15,40138,/"40138_RID1000A_BOARD.Input_J4.4/", | /"DT_ONOFF/", | Modbusparam{15,40138,/"40138_RID1000A_BOARD.Input_J4.4/",/"DT_ONOFF/",},
16 | RID1000A_BOARD.Oil_pressure | DT_REAL_1 | IR2 | 40139 | R |  | Modbusparam{16, | 40139,/"40139_RID1000A_BOARD.Oil_pressure | Modbusparam{16,40139,/"40139_RID1000A_BOARD.Oil_pressure/", | /"DT_REAL_1/", | Modbusparam{16,40139,/"40139_RID1000A_BOARD.Oil_pressure/",/"DT_REAL_1/",},
17 | RID1000A_BOARD.Water_temperature | DT_REAL_1 | IR6 | 40140 | R |  | Modbusparam{17, | 40140,/"40140_RID1000A_BOARD.Water_temperature | Modbusparam{17,40140,/"40140_RID1000A_BOARD.Water_temperature/", | /"DT_REAL_1/", | Modbusparam{17,40140,/"40140_RID1000A_BOARD.Water_temperature/",/"DT_REAL_1/",},
18 | RID1000A_BOARD.Fuel_level | DT_NUMERIC | IR10 | 40141 | R |  | Modbusparam{18, | 40141,/"40141_RID1000A_BOARD.Fuel_level | Modbusparam{18,40141,/"40141_RID1000A_BOARD.Fuel_level/", | /"DT_NUMERIC/", | Modbusparam{18,40141,/"40141_RID1000A_BOARD.Fuel_level/",/"DT_NUMERIC/",},
19 | RID1000A_BOARD.Battery_voltage | DT_REAL_1 | IR14 | 40142 | R |  | Modbusparam{19, | 40142,/"40142_RID1000A_BOARD.Battery_voltage | Modbusparam{19,40142,/"40142_RID1000A_BOARD.Battery_voltage/", | /"DT_REAL_1/", | Modbusparam{19,40142,/"40142_RID1000A_BOARD.Battery_voltage/",/"DT_REAL_1/",},
20 | RID1000A_BOARD.Line_R_voltage_mains | DT_NUMERIC | IR18 | 40143 | R |  | Modbusparam{20, | 40143,/"40143_RID1000A_BOARD.Line_R_voltage_mains | Modbusparam{20,40143,/"40143_RID1000A_BOARD.Line_R_voltage_mains/", | /"DT_NUMERIC/", | Modbusparam{20,40143,/"40143_RID1000A_BOARD.Line_R_voltage_mains/",/"DT_NUMERIC/",},
21 | RID1000A_BOARD.Line_S_voltage_mains | DT_NUMERIC | IR22 | 40144 | R |  | Modbusparam{21, | 40144,/"40144_RID1000A_BOARD.Line_S_voltage_mains | Modbusparam{21,40144,/"40144_RID1000A_BOARD.Line_S_voltage_mains/", | /"DT_NUMERIC/", | Modbusparam{21,40144,/"40144_RID1000A_BOARD.Line_S_voltage_mains/",/"DT_NUMERIC/",},
22 | RID1000A_BOARD.Line_T_voltage_mains | DT_NUMERIC | IR26 | 40145 | R |  | Modbusparam{22, | 40145,/"40145_RID1000A_BOARD.Line_T_voltage_mains | Modbusparam{22,40145,/"40145_RID1000A_BOARD.Line_T_voltage_mains/", | /"DT_NUMERIC/", | Modbusparam{22,40145,/"40145_RID1000A_BOARD.Line_T_voltage_mains/",/"DT_NUMERIC/",},
23 | RID1000A_BOARD.Line_R_voltage_genset | DT_NUMERIC | IR30 | 40146 | R |  | Modbusparam{23, | 40146,/"40146_RID1000A_BOARD.Line_R_voltage_genset | Modbusparam{23,40146,/"40146_RID1000A_BOARD.Line_R_voltage_genset/", | /"DT_NUMERIC/", | Modbusparam{23,40146,/"40146_RID1000A_BOARD.Line_R_voltage_genset/",/"DT_NUMERIC/",},
24 | RID1000A_BOARD.Line_S_voltage_genset | DT_NUMERIC | IR34 | 40147 | R |  | Modbusparam{24, | 40147,/"40147_RID1000A_BOARD.Line_S_voltage_genset | Modbusparam{24,40147,/"40147_RID1000A_BOARD.Line_S_voltage_genset/", | /"DT_NUMERIC/", | Modbusparam{24,40147,/"40147_RID1000A_BOARD.Line_S_voltage_genset/",/"DT_NUMERIC/",},
25 | RID1000A_BOARD.Line_T_voltage_genset | DT_NUMERIC | IR38 | 40148 | R |  | Modbusparam{25, | 40148,/"40148_RID1000A_BOARD.Line_T_voltage_genset | Modbusparam{25,40148,/"40148_RID1000A_BOARD.Line_T_voltage_genset/", | /"DT_NUMERIC/", | Modbusparam{25,40148,/"40148_RID1000A_BOARD.Line_T_voltage_genset/",/"DT_NUMERIC/",},
26 | RID1000A_BOARD.Load_currente_phase_R | DT_NUMERIC | IR42 | 40149 | R |  | Modbusparam{26, | 40149,/"40149_RID1000A_BOARD.Load_currente_phase_R | Modbusparam{26,40149,/"40149_RID1000A_BOARD.Load_currente_phase_R/", | /"DT_NUMERIC/", | Modbusparam{26,40149,/"40149_RID1000A_BOARD.Load_currente_phase_R/",/"DT_NUMERIC/",},
27 | RID1000A_BOARD.Load_current_phase_S | DT_NUMERIC | IR46 | 40150 | R |  | Modbusparam{27, | 40150,/"40150_RID1000A_BOARD.Load_current_phase_S | Modbusparam{27,40150,/"40150_RID1000A_BOARD.Load_current_phase_S/", | /"DT_NUMERIC/", | Modbusparam{27,40150,/"40150_RID1000A_BOARD.Load_current_phase_S/",/"DT_NUMERIC/",},
28 | RID1000A_BOARD.Load_current_phase_T | DT_NUMERIC | IR50 | 40151 | R |  | Modbusparam{28, | 40151,/"40151_RID1000A_BOARD.Load_current_phase_T | Modbusparam{28,40151,/"40151_RID1000A_BOARD.Load_current_phase_T/", | /"DT_NUMERIC/", | Modbusparam{28,40151,/"40151_RID1000A_BOARD.Load_current_phase_T/",/"DT_NUMERIC/",},
29 | RID1000A_BOARD.Frequency_mains | DT_REAL_1 | IR54 | 40152 | R |  | Modbusparam{29, | 40152,/"40152_RID1000A_BOARD.Frequency_mains | Modbusparam{29,40152,/"40152_RID1000A_BOARD.Frequency_mains/", | /"DT_REAL_1/", | Modbusparam{29,40152,/"40152_RID1000A_BOARD.Frequency_mains/",/"DT_REAL_1/",},
30 | RID1000A_BOARD.Frequency_genset | DT_REAL_1 | IR58 | 40153 | R |  | Modbusparam{30, | 40153,/"40153_RID1000A_BOARD.Frequency_genset | Modbusparam{30,40153,/"40153_RID1000A_BOARD.Frequency_genset/", | /"DT_REAL_1/", | Modbusparam{30,40153,/"40153_RID1000A_BOARD.Frequency_genset/",/"DT_REAL_1/",},
31 | RID1000A_BOARD.Active_power_phase_R | DT_REAL_1 | IR62 | 40154 | R |  | Modbusparam{31, | 40154,/"40154_RID1000A_BOARD.Active_power_phase_R | Modbusparam{31,40154,/"40154_RID1000A_BOARD.Active_power_phase_R/", | /"DT_REAL_1/", | Modbusparam{31,40154,/"40154_RID1000A_BOARD.Active_power_phase_R/",/"DT_REAL_1/",},
32 | RID1000A_BOARD.Active_power_phase_S | DT_REAL_1 | IR66 | 40155 | R |  | Modbusparam{32, | 40155,/"40155_RID1000A_BOARD.Active_power_phase_S | Modbusparam{32,40155,/"40155_RID1000A_BOARD.Active_power_phase_S/", | /"DT_REAL_1/", | Modbusparam{32,40155,/"40155_RID1000A_BOARD.Active_power_phase_S/",/"DT_REAL_1/",},
33 | RID1000A_BOARD.Active_power_phase_T | DT_REAL_1 | IR70 | 40156 | R |  | Modbusparam{33, | 40156,/"40156_RID1000A_BOARD.Active_power_phase_T | Modbusparam{33,40156,/"40156_RID1000A_BOARD.Active_power_phase_T/", | /"DT_REAL_1/", | Modbusparam{33,40156,/"40156_RID1000A_BOARD.Active_power_phase_T/",/"DT_REAL_1/",},
34 | RID1000A_BOARD.Phase_voltage_mains | DT_REAL_1 | IR74 | 40157 | R |  | Modbusparam{34, | 40157,/"40157_RID1000A_BOARD.Phase_voltage_mains | Modbusparam{34,40157,/"40157_RID1000A_BOARD.Phase_voltage_mains/", | /"DT_REAL_1/", | Modbusparam{34,40157,/"40157_RID1000A_BOARD.Phase_voltage_mains/",/"DT_REAL_1/",},
35 | RID1000A_BOARD.Phase_voltage_genset | DT_REAL_1 | IR78 | 40158 | R |  | Modbusparam{35, | 40158,/"40158_RID1000A_BOARD.Phase_voltage_genset | Modbusparam{35,40158,/"40158_RID1000A_BOARD.Phase_voltage_genset/", | /"DT_REAL_1/", | Modbusparam{35,40158,/"40158_RID1000A_BOARD.Phase_voltage_genset/",/"DT_REAL_1/",},
36 | RID1000A_BOARD.Apparent_power_phase_R | DT_REAL_1 | IR82 | 40159 | R |  | Modbusparam{36, | 40159,/"40159_RID1000A_BOARD.Apparent_power_phase_R | Modbusparam{36,40159,/"40159_RID1000A_BOARD.Apparent_power_phase_R/", | /"DT_REAL_1/", | Modbusparam{36,40159,/"40159_RID1000A_BOARD.Apparent_power_phase_R/",/"DT_REAL_1/",},
37 | RID1000A_BOARD.Apparent_power_phase_S | DT_REAL_1 | IR86 | 40160 | R |  | Modbusparam{37, | 40160,/"40160_RID1000A_BOARD.Apparent_power_phase_S | Modbusparam{37,40160,/"40160_RID1000A_BOARD.Apparent_power_phase_S/", | /"DT_REAL_1/", | Modbusparam{37,40160,/"40160_RID1000A_BOARD.Apparent_power_phase_S/",/"DT_REAL_1/",},
38 | RID1000A_BOARD.Apparent_power_phase_T | DT_REAL_1 | IR90 | 40161 | R |  | Modbusparam{38, | 40161,/"40161_RID1000A_BOARD.Apparent_power_phase_T | Modbusparam{38,40161,/"40161_RID1000A_BOARD.Apparent_power_phase_T/", | /"DT_REAL_1/", | Modbusparam{38,40161,/"40161_RID1000A_BOARD.Apparent_power_phase_T/",/"DT_REAL_1/",},
39 | RID1000A_BOARD.Reactive_power_phase_R | DT_REAL_1 | IR94 | 40162 | R |  | Modbusparam{39, | 40162,/"40162_RID1000A_BOARD.Reactive_power_phase_R | Modbusparam{39,40162,/"40162_RID1000A_BOARD.Reactive_power_phase_R/", | /"DT_REAL_1/", | Modbusparam{39,40162,/"40162_RID1000A_BOARD.Reactive_power_phase_R/",/"DT_REAL_1/",},
40 | RID1000A_BOARD.Reactive_power_phase_S | DT_REAL_1 | IR98 | 40163 | R |  | Modbusparam{40, | 40163,/"40163_RID1000A_BOARD.Reactive_power_phase_S | Modbusparam{40,40163,/"40163_RID1000A_BOARD.Reactive_power_phase_S/", | /"DT_REAL_1/", | Modbusparam{40,40163,/"40163_RID1000A_BOARD.Reactive_power_phase_S/",/"DT_REAL_1/",},
41 | RID1000A_BOARD.Reactive_power_phase_T | DT_REAL_1 | IR102 | 40164 | R |  | Modbusparam{41, | 40164,/"40164_RID1000A_BOARD.Reactive_power_phase_T | Modbusparam{41,40164,/"40164_RID1000A_BOARD.Reactive_power_phase_T/", | /"DT_REAL_1/", | Modbusparam{41,40164,/"40164_RID1000A_BOARD.Reactive_power_phase_T/",/"DT_REAL_1/",},
42 | RID1000A_BOARD.Reactive_power_totale | DT_REAL_1 | IR106 | 40165 | R |  | Modbusparam{42, | 40165,/"40165_RID1000A_BOARD.Reactive_power_totale | Modbusparam{42,40165,/"40165_RID1000A_BOARD.Reactive_power_totale/", | /"DT_REAL_1/", | Modbusparam{42,40165,/"40165_RID1000A_BOARD.Reactive_power_totale/",/"DT_REAL_1/",},
43 | RID1000A_BOARD.Power_factor_phase_R | DT_REAL_2 | IR110 | 40166 | R |  | Modbusparam{43, | 40166,/"40166_RID1000A_BOARD.Power_factor_phase_R | Modbusparam{43,40166,/"40166_RID1000A_BOARD.Power_factor_phase_R/", | /"DT_REAL_2/", | Modbusparam{43,40166,/"40166_RID1000A_BOARD.Power_factor_phase_R/",/"DT_REAL_2/",},
44 | RID1000A_BOARD.Power_factor_phase_S | DT_REAL_2 | IR114 | 40167 | R |  | Modbusparam{44, | 40167,/"40167_RID1000A_BOARD.Power_factor_phase_S | Modbusparam{44,40167,/"40167_RID1000A_BOARD.Power_factor_phase_S/", | /"DT_REAL_2/", | Modbusparam{44,40167,/"40167_RID1000A_BOARD.Power_factor_phase_S/",/"DT_REAL_2/",},
45 | RID1000A_BOARD.Power_factor_phase_T | DT_REAL_2 | IR118 | 40168 | R |  | Modbusparam{45, | 40168,/"40168_RID1000A_BOARD.Power_factor_phase_T | Modbusparam{45,40168,/"40168_RID1000A_BOARD.Power_factor_phase_T/", | /"DT_REAL_2/", | Modbusparam{45,40168,/"40168_RID1000A_BOARD.Power_factor_phase_T/",/"DT_REAL_2/",},
46 | RID1000A_BOARD.Wrong_phase_sequence_mains | DT_ONOFF | I0.5 | 40169 | R |  | Modbusparam{46, | 40169,/"40169_RID1000A_BOARD.Wrong_phase_sequence_mains | Modbusparam{46,40169,/"40169_RID1000A_BOARD.Wrong_phase_sequence_mains/", | /"DT_ONOFF/", | Modbusparam{46,40169,/"40169_RID1000A_BOARD.Wrong_phase_sequence_mains/",/"DT_ONOFF/",},
47 | RID1000A_BOARD.Wrong_phase_sequence_genset | DT_ONOFF | I0.6 | 40170 | R |  | Modbusparam{47, | 40170,/"40170_RID1000A_BOARD.Wrong_phase_sequence_genset | Modbusparam{47,40170,/"40170_RID1000A_BOARD.Wrong_phase_sequence_genset/", | /"DT_ONOFF/", | Modbusparam{47,40170,/"40170_RID1000A_BOARD.Wrong_phase_sequence_genset/",/"DT_ONOFF/",},
48 | RID1000A_BOARD.Emergency | DT_ONOFF | I0.7 | 40171 | R |  | Modbusparam{48, | 40171,/"40171_RID1000A_BOARD.Emergency | Modbusparam{48,40171,/"40171_RID1000A_BOARD.Emergency/", | /"DT_ONOFF/", | Modbusparam{48,40171,/"40171_RID1000A_BOARD.Emergency/",/"DT_ONOFF/",},
49 | RID1000A_BOARD.Total_apparent_power | DT_REAL_1 | IR122 | 40174 | R |  | Modbusparam{49, | 40174,/"40174_RID1000A_BOARD.Total_apparent_power | Modbusparam{49,40174,/"40174_RID1000A_BOARD.Total_apparent_power/", | /"DT_REAL_1/", | Modbusparam{49,40174,/"40174_RID1000A_BOARD.Total_apparent_power/",/"DT_REAL_1/",},
50 | RID1000A_BOARD.Total_active_power | DT_REAL_1 | IR126 | 40175 | R |  | Modbusparam{50, | 40175,/"40175_RID1000A_BOARD.Total_active_power | Modbusparam{50,40175,/"40175_RID1000A_BOARD.Total_active_power/", | /"DT_REAL_1/", | Modbusparam{50,40175,/"40175_RID1000A_BOARD.Total_active_power/",/"DT_REAL_1/",},
51 | RID1000A_BOARD.Total_power_factor | DT_REAL_2 | IR130 | 40176 | R |  | Modbusparam{51, | 40176,/"40176_RID1000A_BOARD.Total_power_factor | Modbusparam{51,40176,/"40176_RID1000A_BOARD.Total_power_factor/", | /"DT_REAL_2/", | Modbusparam{51,40176,/"40176_RID1000A_BOARD.Total_power_factor/",/"DT_REAL_2/",},
52 | RID1000A_BOARD.Higher_consumption_current | DT_REAL_1 | IR134 | 40177 | R |  | Modbusparam{52, | 40177,/"40177_RID1000A_BOARD.Higher_consumption_current | Modbusparam{52,40177,/"40177_RID1000A_BOARD.Higher_consumption_current/", | /"DT_REAL_1/", | Modbusparam{52,40177,/"40177_RID1000A_BOARD.Higher_consumption_current/",/"DT_REAL_1/",},
53 | RID1000A_BOARD.Frequency_PICKUP_(Hz) | DT_NUMERIC | IR138 | 40178 | R |  | Modbusparam{53, | 40178,/"40178_RID1000A_BOARD.Frequency_PICKUP_(Hz) | Modbusparam{53,40178,/"40178_RID1000A_BOARD.Frequency_PICKUP_(Hz)/", | /"DT_NUMERIC/", | Modbusparam{53,40178,/"40178_RID1000A_BOARD.Frequency_PICKUP_(Hz)/",/"DT_NUMERIC/",},
54 | RID1000A_BOARD.Voltage_D+ | DT_REAL_1 | IR142 | 40179 | R |  | Modbusparam{54, | 40179,/"40179_RID1000A_BOARD.Voltage_D+ | Modbusparam{54,40179,/"40179_RID1000A_BOARD.Voltage_D+/", | /"DT_REAL_1/", | Modbusparam{54,40179,/"40179_RID1000A_BOARD.Voltage_D+/",/"DT_REAL_1/",},
55 | RID1000A_BOARD.Phase_voltage_R-S_mains | DT_NUMERIC | IR146 | 40180 | R |  | Modbusparam{55, | 40180,/"40180_RID1000A_BOARD.Phase_voltage_R-S_mains | Modbusparam{55,40180,/"40180_RID1000A_BOARD.Phase_voltage_R-S_mains/", | /"DT_NUMERIC/", | Modbusparam{55,40180,/"40180_RID1000A_BOARD.Phase_voltage_R-S_mains/",/"DT_NUMERIC/",},
56 | RID1000A_BOARD.Phase_voltage_S-T_mains | DT_NUMERIC | IR150 | 40181 | R |  | Modbusparam{56, | 40181,/"40181_RID1000A_BOARD.Phase_voltage_S-T_mains | Modbusparam{56,40181,/"40181_RID1000A_BOARD.Phase_voltage_S-T_mains/", | /"DT_NUMERIC/", | Modbusparam{56,40181,/"40181_RID1000A_BOARD.Phase_voltage_S-T_mains/",/"DT_NUMERIC/",},
57 | RID1000A_BOARD.Phase_voltage_T-R_mains | DT_NUMERIC | IR154 | 40182 | R |  | Modbusparam{57, | 40182,/"40182_RID1000A_BOARD.Phase_voltage_T-R_mains | Modbusparam{57,40182,/"40182_RID1000A_BOARD.Phase_voltage_T-R_mains/", | /"DT_NUMERIC/", | Modbusparam{57,40182,/"40182_RID1000A_BOARD.Phase_voltage_T-R_mains/",/"DT_NUMERIC/",},
58 | RID1000A_BOARD.Phase_voltage_R-S_genset | DT_NUMERIC | IR158 | 40183 | R |  | Modbusparam{58, | 40183,/"40183_RID1000A_BOARD.Phase_voltage_R-S_genset | Modbusparam{58,40183,/"40183_RID1000A_BOARD.Phase_voltage_R-S_genset/", | /"DT_NUMERIC/", | Modbusparam{58,40183,/"40183_RID1000A_BOARD.Phase_voltage_R-S_genset/",/"DT_NUMERIC/",},
59 | RID1000A_BOARD.Phase_voltage_S-T_genset | DT_NUMERIC | IR162 | 40184 | R |  | Modbusparam{59, | 40184,/"40184_RID1000A_BOARD.Phase_voltage_S-T_genset | Modbusparam{59,40184,/"40184_RID1000A_BOARD.Phase_voltage_S-T_genset/", | /"DT_NUMERIC/", | Modbusparam{59,40184,/"40184_RID1000A_BOARD.Phase_voltage_S-T_genset/",/"DT_NUMERIC/",},
60 | RID1000A_BOARD.Phase_voltage_T-R_genset | DT_NUMERIC | IR166 | 40185 | R |  | Modbusparam{60, | 40185,/"40185_RID1000A_BOARD.Phase_voltage_T-R_genset | Modbusparam{60,40185,/"40185_RID1000A_BOARD.Phase_voltage_T-R_genset/", | /"DT_NUMERIC/", | Modbusparam{60,40185,/"40185_RID1000A_BOARD.Phase_voltage_T-R_genset/",/"DT_NUMERIC/",},
61 | RID1000A_BOARD.Rpm_(SPN_190) | DT_NUMERIC | IR300 | 40186 | R |  | Modbusparam{61, | 40186,/"40186_RID1000A_BOARD.Rpm_(SPN_190) | Modbusparam{61,40186,/"40186_RID1000A_BOARD.Rpm_(SPN_190)/", | /"DT_NUMERIC/", | Modbusparam{61,40186,/"40186_RID1000A_BOARD.Rpm_(SPN_190)/",/"DT_NUMERIC/",},
62 | RID1000A_BOARD.Oil_pressure_(SPN_100) | DT_REAL_1 | IR304 | 40187 | R |  | Modbusparam{62, | 40187,/"40187_RID1000A_BOARD.Oil_pressure_(SPN_100) | Modbusparam{62,40187,/"40187_RID1000A_BOARD.Oil_pressure_(SPN_100)/", | /"DT_REAL_1/", | Modbusparam{62,40187,/"40187_RID1000A_BOARD.Oil_pressure_(SPN_100)/",/"DT_REAL_1/",},
63 | RID1000A_BOARD.Engine_temperature_(SPN_110) | DT_REAL_1 | IR308 | 40188 | R |  | Modbusparam{63, | 40188,/"40188_RID1000A_BOARD.Engine_temperature_(SPN_110) | Modbusparam{63,40188,/"40188_RID1000A_BOARD.Engine_temperature_(SPN_110)/", | /"DT_REAL_1/", | Modbusparam{63,40188,/"40188_RID1000A_BOARD.Engine_temperature_(SPN_110)/",/"DT_REAL_1/",},
64 | RID1000A_BOARD.Fuel_temperature_(SPN_174) | DT_REAL_1 | IR312 | 40189 | R |  | Modbusparam{64, | 40189,/"40189_RID1000A_BOARD.Fuel_temperature_(SPN_174) | Modbusparam{64,40189,/"40189_RID1000A_BOARD.Fuel_temperature_(SPN_174)/", | /"DT_REAL_1/", | Modbusparam{64,40189,/"40189_RID1000A_BOARD.Fuel_temperature_(SPN_174)/",/"DT_REAL_1/",},
65 | RID1000A_BOARD.Oil_temperature_(SPN_175) | DT_REAL_1 | IR316 | 40190 | R |  | Modbusparam{65, | 40190,/"40190_RID1000A_BOARD.Oil_temperature_(SPN_175) | Modbusparam{65,40190,/"40190_RID1000A_BOARD.Oil_temperature_(SPN_175)/", | /"DT_REAL_1/", | Modbusparam{65,40190,/"40190_RID1000A_BOARD.Oil_temperature_(SPN_175)/",/"DT_REAL_1/",},
66 | RID1000A_BOARD.Fuel_pressure_(SPN_094) | DT_REAL_1 | IR320 | 40191 | R |  | Modbusparam{66, | 40191,/"40191_RID1000A_BOARD.Fuel_pressure_(SPN_094) | Modbusparam{66,40191,/"40191_RID1000A_BOARD.Fuel_pressure_(SPN_094)/", | /"DT_REAL_1/", | Modbusparam{66,40191,/"40191_RID1000A_BOARD.Fuel_pressure_(SPN_094)/",/"DT_REAL_1/",},
67 | RID1000A_BOARD.Oil_level_(SPN_098) | DT_REAL_1 | IR324 | 40192 | R |  | Modbusparam{67, | 40192,/"40192_RID1000A_BOARD.Oil_level_(SPN_098) | Modbusparam{67,40192,/"40192_RID1000A_BOARD.Oil_level_(SPN_098)/", | /"DT_REAL_1/", | Modbusparam{67,40192,/"40192_RID1000A_BOARD.Oil_level_(SPN_098)/",/"DT_REAL_1/",},
68 | RID1000A_BOARD.Carter_pressure_(SPN_101) | DT_REAL_1 | IR328 | 40193 | R |  | Modbusparam{68, | 40193,/"40193_RID1000A_BOARD.Carter_pressure_(SPN_101) | Modbusparam{68,40193,/"40193_RID1000A_BOARD.Carter_pressure_(SPN_101)/", | /"DT_REAL_1/", | Modbusparam{68,40193,/"40193_RID1000A_BOARD.Carter_pressure_(SPN_101)/",/"DT_REAL_1/",},
69 | RID1000A_BOARD.Coolant_pressure_(SPN_109) | DT_REAL_1 | IR332 | 40194 | R |  | Modbusparam{69, | 40194,/"40194_RID1000A_BOARD.Coolant_pressure_(SPN_109) | Modbusparam{69,40194,/"40194_RID1000A_BOARD.Coolant_pressure_(SPN_109)/", | /"DT_REAL_1/", | Modbusparam{69,40194,/"40194_RID1000A_BOARD.Coolant_pressure_(SPN_109)/",/"DT_REAL_1/",},
70 | RID1000A_BOARD.Coolant_level_(SPN_111) | DT_REAL_1 | IR336 | 40195 | R |  | Modbusparam{70, | 40195,/"40195_RID1000A_BOARD.Coolant_level_(SPN_111) | Modbusparam{70,40195,/"40195_RID1000A_BOARD.Coolant_level_(SPN_111)/", | /"DT_REAL_1/", | Modbusparam{70,40195,/"40195_RID1000A_BOARD.Coolant_level_(SPN_111)/",/"DT_REAL_1/",},
71 | RID1000A_BOARD.Total_work_hours_(SPN_247) | DT_NUMERIC | IR340 | 40196 | R |  | Modbusparam{71, | 40196,/"40196_RID1000A_BOARD.Total_work_hours_(SPN_247) | Modbusparam{71,40196,/"40196_RID1000A_BOARD.Total_work_hours_(SPN_247)/", | /"DT_NUMERIC/", | Modbusparam{71,40196,/"40196_RID1000A_BOARD.Total_work_hours_(SPN_247)/",/"DT_NUMERIC/",},
72 | RID1000A_BOARD.Turbo_pressure_(SPN_102) | DT_REAL_1 | IR344 | 40197 | R |  | Modbusparam{72, | 40197,/"40197_RID1000A_BOARD.Turbo_pressure_(SPN_102) | Modbusparam{72,40197,/"40197_RID1000A_BOARD.Turbo_pressure_(SPN_102)/", | /"DT_REAL_1/", | Modbusparam{72,40197,/"40197_RID1000A_BOARD.Turbo_pressure_(SPN_102)/",/"DT_REAL_1/",},
73 | RID1000A_BOARD.Turbo_temeprature_(SPN_105) | DT_NUMERIC | IR348 | 40198 | R |  | Modbusparam{73, | 40198,/"40198_RID1000A_BOARD.Turbo_temeprature_(SPN_105) | Modbusparam{73,40198,/"40198_RID1000A_BOARD.Turbo_temeprature_(SPN_105)/", | /"DT_NUMERIC/", | Modbusparam{73,40198,/"40198_RID1000A_BOARD.Turbo_temeprature_(SPN_105)/",/"DT_NUMERIC/",},
74 | RID1000A_BOARD.Instant_consumption_(SPN_183) | DT_REAL_1 | IR352 | 40199 | R |  | Modbusparam{74, | 40199,/"40199_RID1000A_BOARD.Instant_consumption_(SPN_183) | Modbusparam{74,40199,/"40199_RID1000A_BOARD.Instant_consumption_(SPN_183)/", | /"DT_REAL_1/", | Modbusparam{74,40199,/"40199_RID1000A_BOARD.Instant_consumption_(SPN_183)/",/"DT_REAL_1/",},
75 | RID1000A_BOARD.Torque_(SPN_513) | DT_NUMERIC | IR356 | 40200 | R |  | Modbusparam{75, | 40200,/"40200_RID1000A_BOARD.Torque_(SPN_513) | Modbusparam{75,40200,/"40200_RID1000A_BOARD.Torque_(SPN_513)/", | /"DT_NUMERIC/", | Modbusparam{75,40200,/"40200_RID1000A_BOARD.Torque_(SPN_513)/",/"DT_NUMERIC/",},
76 | RID1000A_BOARD.Torque_request_(SPN_512) | DT_NUMERIC | IR360 | 40201 | R |  | Modbusparam{76, | 40201,/"40201_RID1000A_BOARD.Torque_request_(SPN_512) | Modbusparam{76,40201,/"40201_RID1000A_BOARD.Torque_request_(SPN_512)/", | /"DT_NUMERIC/", | Modbusparam{76,40201,/"40201_RID1000A_BOARD.Torque_request_(SPN_512)/",/"DT_NUMERIC/",},
77 | RID1000A_BOARD.Water_level_(SPN_97) | DT_NUMERIC | IR364 | 40202 | R |  | Modbusparam{77, | 40202,/"40202_RID1000A_BOARD.Water_level_(SPN_97) | Modbusparam{77,40202,/"40202_RID1000A_BOARD.Water_level_(SPN_97)/", | /"DT_NUMERIC/", | Modbusparam{77,40202,/"40202_RID1000A_BOARD.Water_level_(SPN_97)/",/"DT_NUMERIC/",},
78 | RID1000A_BOARD.Accelerator_position_(%)_(SPN_91) | DT_NUMERIC | IR368 | 40203 | R |  | Modbusparam{78, | 40203,/"40203_RID1000A_BOARD.Accelerator_position_(%)_(SPN_91) | Modbusparam{78,40203,/"40203_RID1000A_BOARD.Accelerator_position_(%)_(SPN_91)/", | /"DT_NUMERIC/", | Modbusparam{78,40203,/"40203_RID1000A_BOARD.Accelerator_position_(%)_(SPN_91)/",/"DT_NUMERIC/",},
79 | RID1000A_BOARD.Load_percentage_(SPN_92) | DT_NUMERIC | IR372 | 40204 | R |  | Modbusparam{79, | 40204,/"40204_RID1000A_BOARD.Load_percentage_(SPN_92) | Modbusparam{79,40204,/"40204_RID1000A_BOARD.Load_percentage_(SPN_92)/", | /"DT_NUMERIC/", | Modbusparam{79,40204,/"40204_RID1000A_BOARD.Load_percentage_(SPN_92)/",/"DT_NUMERIC/",},
80 | RID1000A_BOARD.Battery_voltage_(SPN_158) | DT_REAL_1 | IR376 | 40205 | R |  | Modbusparam{80, | 40205,/"40205_RID1000A_BOARD.Battery_voltage_(SPN_158) | Modbusparam{80,40205,/"40205_RID1000A_BOARD.Battery_voltage_(SPN_158)/", | /"DT_REAL_1/", | Modbusparam{80,40205,/"40205_RID1000A_BOARD.Battery_voltage_(SPN_158)/",/"DT_REAL_1/",},
81 | RID1000A_BOARD.Aspiration_pressure_(SPN_106) | DT_REAL_1 | IR380 | 40206 | R |  | Modbusparam{81, | 40206,/"40206_RID1000A_BOARD.Aspiration_pressure_(SPN_106) | Modbusparam{81,40206,/"40206_RID1000A_BOARD.Aspiration_pressure_(SPN_106)/", | /"DT_REAL_1/", | Modbusparam{81,40206,/"40206_RID1000A_BOARD.Aspiration_pressure_(SPN_106)/",/"DT_REAL_1/",},
82 | RID1000A_BOARD.Atmospheric_pressure_(SPN_108) | DT_REAL_1 | IR384 | 40207 | R |  | Modbusparam{82, | 40207,/"40207_RID1000A_BOARD.Atmospheric_pressure_(SPN_108) | Modbusparam{82,40207,/"40207_RID1000A_BOARD.Atmospheric_pressure_(SPN_108)/", | /"DT_REAL_1/", | Modbusparam{82,40207,/"40207_RID1000A_BOARD.Atmospheric_pressure_(SPN_108)/",/"DT_REAL_1/",},
83 | RID1000A_BOARD.Discharge_temperature_(SPN_173) | DT_REAL_1 | IR388 | 40208 | R |  | Modbusparam{83, | 40208,/"40208_RID1000A_BOARD.Discharge_temperature_(SPN_173) | Modbusparam{83,40208,/"40208_RID1000A_BOARD.Discharge_temperature_(SPN_173)/", | /"DT_REAL_1/", | Modbusparam{83,40208,/"40208_RID1000A_BOARD.Discharge_temperature_(SPN_173)/",/"DT_REAL_1/",},
84 | RID1000A_BOARD.DTC_-_SPN | DT_NUMERIC | IR392 | 40209 | R |  | Modbusparam{84, | 40209,/"40209_RID1000A_BOARD.DTC_-_SPN | Modbusparam{84,40209,/"40209_RID1000A_BOARD.DTC_-_SPN/", | /"DT_NUMERIC/", | Modbusparam{84,40209,/"40209_RID1000A_BOARD.DTC_-_SPN/",/"DT_NUMERIC/",},
85 | RID1000A_BOARD.DTC_-_FMI | DT_NUMERIC | IR396 | 40210 | R |  | Modbusparam{85, | 40210,/"40210_RID1000A_BOARD.DTC_-_FMI | Modbusparam{85,40210,/"40210_RID1000A_BOARD.DTC_-_FMI/", | /"DT_NUMERIC/", | Modbusparam{85,40210,/"40210_RID1000A_BOARD.DTC_-_FMI/",/"DT_NUMERIC/",},
86 | RID1000A_BOARD.Start_output | DT_ONOFF | U0.0 | 40215 | R |  | Modbusparam{86, | 40215,/"40215_RID1000A_BOARD.Start_output | Modbusparam{86,40215,/"40215_RID1000A_BOARD.Start_output/", | /"DT_ONOFF/", | Modbusparam{86,40215,/"40215_RID1000A_BOARD.Start_output/",/"DT_ONOFF/",},
87 | RID1000A_BOARD.EV_output | DT_ONOFF | U0.1 | 40216 | R |  | Modbusparam{87, | 40216,/"40216_RID1000A_BOARD.EV_output | Modbusparam{87,40216,/"40216_RID1000A_BOARD.EV_output/", | /"DT_ONOFF/", | Modbusparam{87,40216,/"40216_RID1000A_BOARD.EV_output/",/"DT_ONOFF/",},
88 | RID1000A_BOARD.Genset_contactor | DT_ONOFF | U0.2 | 40217 | R |  | Modbusparam{88, | 40217,/"40217_RID1000A_BOARD.Genset_contactor | Modbusparam{88,40217,/"40217_RID1000A_BOARD.Genset_contactor/", | /"DT_ONOFF/", | Modbusparam{88,40217,/"40217_RID1000A_BOARD.Genset_contactor/",/"DT_ONOFF/",},
89 | RID1000A_BOARD.Mains_contactor | DT_ONOFF | U0.3 | 40218 | R |  | Modbusparam{89, | 40218,/"40218_RID1000A_BOARD.Mains_contactor | Modbusparam{89,40218,/"40218_RID1000A_BOARD.Mains_contactor/", | /"DT_ONOFF/", | Modbusparam{89,40218,/"40218_RID1000A_BOARD.Mains_contactor/",/"DT_ONOFF/",},
90 | RID1000A_BOARD.Excitation | DT_ONOFF | U0.4 | 40219 | R |  | Modbusparam{90, | 40219,/"40219_RID1000A_BOARD.Excitation | Modbusparam{90,40219,/"40219_RID1000A_BOARD.Excitation/", | /"DT_ONOFF/", | Modbusparam{90,40219,/"40219_RID1000A_BOARD.Excitation/",/"DT_ONOFF/",},
91 | RID1000A_BOARD.Out_J5.11 | DT_ONOFF | U1.0 | 40220 | R |  | Modbusparam{91, | 40220,/"40220_RID1000A_BOARD.Out_J5.11 | Modbusparam{91,40220,/"40220_RID1000A_BOARD.Out_J5.11/", | /"DT_ONOFF/", | Modbusparam{91,40220,/"40220_RID1000A_BOARD.Out_J5.11/",/"DT_ONOFF/",},
92 | RID1000A_BOARD.Out_J5.10 | DT_ONOFF | U1.1 | 40221 | R |  | Modbusparam{92, | 40221,/"40221_RID1000A_BOARD.Out_J5.10 | Modbusparam{92,40221,/"40221_RID1000A_BOARD.Out_J5.10/", | /"DT_ONOFF/", | Modbusparam{92,40221,/"40221_RID1000A_BOARD.Out_J5.10/",/"DT_ONOFF/",},
93 | RID1000A_BOARD.Out_J5.9 | DT_ONOFF | U1.2 | 40222 | R |  | Modbusparam{93, | 40222,/"40222_RID1000A_BOARD.Out_J5.9 | Modbusparam{93,40222,/"40222_RID1000A_BOARD.Out_J5.9/", | /"DT_ONOFF/", | Modbusparam{93,40222,/"40222_RID1000A_BOARD.Out_J5.9/",/"DT_ONOFF/",},
94 | RID1000A_BOARD.Out_J5.8 | DT_ONOFF | U1.3 | 40223 | R |  | Modbusparam{94, | 40223,/"40223_RID1000A_BOARD.Out_J5.8 | Modbusparam{94,40223,/"40223_RID1000A_BOARD.Out_J5.8/", | /"DT_ONOFF/", | Modbusparam{94,40223,/"40223_RID1000A_BOARD.Out_J5.8/",/"DT_ONOFF/",},
95 | RID1000A_BOARD.Led_ON/OFF | DT_ONOFF | U2.0 | 40224 | R |  | Modbusparam{95, | 40224,/"40224_RID1000A_BOARD.Led_ON/OFF | Modbusparam{95,40224,/"40224_RID1000A_BOARD.Led_ON/OFF/", | /"DT_ONOFF/", | Modbusparam{95,40224,/"40224_RID1000A_BOARD.Led_ON/OFF/",/"DT_ONOFF/",},
96 | RID1000A_BOARD.Led_KG1 | DT_ONOFF | U2.1 | 40225 | R |  | Modbusparam{96, | 40225,/"40225_RID1000A_BOARD.Led_KG1 | Modbusparam{96,40225,/"40225_RID1000A_BOARD.Led_KG1/", | /"DT_ONOFF/", | Modbusparam{96,40225,/"40225_RID1000A_BOARD.Led_KG1/",/"DT_ONOFF/",},
97 | RID1000A_BOARD.Led_RES | DT_ONOFF | U2.2 | 40226 | R |  | Modbusparam{97, | 40226,/"40226_RID1000A_BOARD.Led_RES | Modbusparam{97,40226,/"40226_RID1000A_BOARD.Led_RES/", | /"DT_ONOFF/", | Modbusparam{97,40226,/"40226_RID1000A_BOARD.Led_RES/",/"DT_ONOFF/",},
98 | RID1000A_BOARD.Led_AUT | DT_ONOFF | U2.3 | 40227 | R |  | Modbusparam{98, | 40227,/"40227_RID1000A_BOARD.Led_AUT | Modbusparam{98,40227,/"40227_RID1000A_BOARD.Led_AUT/", | /"DT_ONOFF/", | Modbusparam{98,40227,/"40227_RID1000A_BOARD.Led_AUT/",/"DT_ONOFF/",},
99 | RID1000A_BOARD.Led_KR | DT_ONOFF | U2.4 | 40228 | R |  | Modbusparam{99, | 40228,/"40228_RID1000A_BOARD.Led_KR | Modbusparam{99,40228,/"40228_RID1000A_BOARD.Led_KR/", | /"DT_ONOFF/", | Modbusparam{99,40228,/"40228_RID1000A_BOARD.Led_KR/",/"DT_ONOFF/",},
100 | RID1000A_BOARD.Led_KR1 | DT_ONOFF | U2.5 | 40229 | R |  | Modbusparam{100, | 40229,/"40229_RID1000A_BOARD.Led_KR1 | Modbusparam{100,40229,/"40229_RID1000A_BOARD.Led_KR1/", | /"DT_ONOFF/", | Modbusparam{100,40229,/"40229_RID1000A_BOARD.Led_KR1/",/"DT_ONOFF/",},
101 | RID1000A_BOARD.Led_KG | DT_ONOFF | U2.6 | 40230 | R |  | Modbusparam{101, | 40230,/"40230_RID1000A_BOARD.Led_KG | Modbusparam{101,40230,/"40230_RID1000A_BOARD.Led_KG/", | /"DT_ONOFF/", | Modbusparam{101,40230,/"40230_RID1000A_BOARD.Led_KG/",/"DT_ONOFF/",},
102 | RID1000A_BOARD.Led_TEST | DT_ONOFF | U2.7 | 40231 | R |  | Modbusparam{102, | 40231,/"40231_RID1000A_BOARD.Led_TEST | Modbusparam{102,40231,/"40231_RID1000A_BOARD.Led_TEST/", | /"DT_ONOFF/", | Modbusparam{102,40231,/"40231_RID1000A_BOARD.Led_TEST/",/"DT_ONOFF/",},
103 | RID1000A_BOARD.Led_MAN | DT_ONOFF | U3.0 | 40232 | R |  | Modbusparam{103, | 40232,/"40232_RID1000A_BOARD.Led_MAN | Modbusparam{103,40232,/"40232_RID1000A_BOARD.Led_MAN/", | /"DT_ONOFF/", | Modbusparam{103,40232,/"40232_RID1000A_BOARD.Led_MAN/",/"DT_ONOFF/",},
104 | RID1000A_BOARD.Led_ALARM | DT_ONOFF | U3.1 | 40233 | R |  | Modbusparam{104, | 40233,/"40233_RID1000A_BOARD.Led_ALARM | Modbusparam{104,40233,/"40233_RID1000A_BOARD.Led_ALARM/", | /"DT_ONOFF/", | Modbusparam{104,40233,/"40233_RID1000A_BOARD.Led_ALARM/",/"DT_ONOFF/",},
105 | RID1000A_BOARD.Full_memory | DT_ONOFF | I500.0 | 40236 | R |  | Modbusparam{105, | 40236,/"40236_RID1000A_BOARD.Full_memory | Modbusparam{105,40236,/"40236_RID1000A_BOARD.Full_memory/", | /"DT_ONOFF/", | Modbusparam{105,40236,/"40236_RID1000A_BOARD.Full_memory/",/"DT_ONOFF/",},
163 | GLOBAL_INPUTS.Engine_temperature | DT_REAL_1 | MR102 | 40422 | R | 62 | Modbusparam{163, | 40422,/"40422_GLOBAL_INPUTS.Engine_temperature | Modbusparam{163,40422,/"40422_GLOBAL_INPUTS.Engine_temperature/", | /"DT_REAL_1/", | Modbusparam{163,40422,/"40422_GLOBAL_INPUTS.Engine_temperature/",/"DT_REAL_1/",},
164 | GLOBAL_INPUTS.Digital_engine_temperature | DT_ONOFF | M100.0 | 40423 | R |  | Modbusparam{164, | 40423,/"40423_GLOBAL_INPUTS.Digital_engine_temperature | Modbusparam{164,40423,/"40423_GLOBAL_INPUTS.Digital_engine_temperature/", | /"DT_ONOFF/", | Modbusparam{164,40423,/"40423_GLOBAL_INPUTS.Digital_engine_temperature/",/"DT_ONOFF/",},
165 | GLOBAL_INPUTS.Input_D+ | DT_REAL_1 | MR114 | 40424 | R |  | Modbusparam{165, | 40424,/"40424_GLOBAL_INPUTS.Input_D+ | Modbusparam{165,40424,/"40424_GLOBAL_INPUTS.Input_D+/", | /"DT_REAL_1/", | Modbusparam{165,40424,/"40424_GLOBAL_INPUTS.Input_D+/",/"DT_REAL_1/",},
166 | GLOBAL_INPUTS.Input_Pick_up | DT_REAL_1 | MR118 | 40425 | R |  | Modbusparam{166, | 40425,/"40425_GLOBAL_INPUTS.Input_Pick_up | Modbusparam{166,40425,/"40425_GLOBAL_INPUTS.Input_Pick_up/", | /"DT_REAL_1/", | Modbusparam{166,40425,/"40425_GLOBAL_INPUTS.Input_Pick_up/",/"DT_REAL_1/",},
167 | GLOBAL_INPUTS.Input_SAPRISA | DT_REAL_1 | MR122 | 40426 | R |  | Modbusparam{167, | 40426,/"40426_GLOBAL_INPUTS.Input_SAPRISA | Modbusparam{167,40426,/"40426_GLOBAL_INPUTS.Input_SAPRISA/", | /"DT_REAL_1/", | Modbusparam{167,40426,/"40426_GLOBAL_INPUTS.Input_SAPRISA/",/"DT_REAL_1/",},
168 | GLOBAL_INPUTS.Input_W | DT_REAL_1 | MR126 | 40427 | R |  | Modbusparam{168, | 40427,/"40427_GLOBAL_INPUTS.Input_W | Modbusparam{168,40427,/"40427_GLOBAL_INPUTS.Input_W/", | /"DT_REAL_1/", | Modbusparam{168,40427,/"40427_GLOBAL_INPUTS.Input_W/",/"DT_REAL_1/",},
169 | GLOBAL_INPUTS.Oil_pressure | DT_REAL_1 | MR110 | 40428 | R |  | Modbusparam{169, | 40428,/"40428_GLOBAL_INPUTS.Oil_pressure | Modbusparam{169,40428,/"40428_GLOBAL_INPUTS.Oil_pressure/", | /"DT_REAL_1/", | Modbusparam{169,40428,/"40428_GLOBAL_INPUTS.Oil_pressure/",/"DT_REAL_1/",},
170 | GLOBAL_INPUTS.Digital_oil_pressure | DT_ONOFF | M100.2 | 40429 | R |  | Modbusparam{170, | 40429,/"40429_GLOBAL_INPUTS.Digital_oil_pressure | Modbusparam{170,40429,/"40429_GLOBAL_INPUTS.Digital_oil_pressure/", | /"DT_ONOFF/", | Modbusparam{170,40429,/"40429_GLOBAL_INPUTS.Digital_oil_pressure/",/"DT_ONOFF/",},
171 | GLOBAL_INPUTS.Fuel_level_(%) | DT_REAL_1 | MR106 | 40430 | R |  | Modbusparam{171, | 40430,/"40430_GLOBAL_INPUTS.Fuel_level_(%) | Modbusparam{171,40430,/"40430_GLOBAL_INPUTS.Fuel_level_(%)/", | /"DT_REAL_1/", | Modbusparam{171,40430,/"40430_GLOBAL_INPUTS.Fuel_level_(%)/",/"DT_REAL_1/",},
172 | GLOBAL_INPUTS.Low_fuel_level_digital | DT_ONOFF | M100.1 | 40431 | R |  | Modbusparam{172, | 40431,/"40431_GLOBAL_INPUTS.Low_fuel_level_digital | Modbusparam{172,40431,/"40431_GLOBAL_INPUTS.Low_fuel_level_digital/", | /"DT_ONOFF/", | Modbusparam{172,40431,/"40431_GLOBAL_INPUTS.Low_fuel_level_digital/",/"DT_ONOFF/",},
173 | GLOBAL_INPUTS.Battery_voltage | DT_REAL_1 | MR130 | 40432 | R |  | Modbusparam{173, | 40432,/"40432_GLOBAL_INPUTS.Battery_voltage | Modbusparam{173,40432,/"40432_GLOBAL_INPUTS.Battery_voltage/", | /"DT_REAL_1/", | Modbusparam{173,40432,/"40432_GLOBAL_INPUTS.Battery_voltage/",/"DT_REAL_1/",},
174 | GLOBAL_INPUTS.Phase_voltage | DT_REAL_1 | MR138 | 40433 | R |  | Modbusparam{174, | 40433,/"40433_GLOBAL_INPUTS.Phase_voltage | Modbusparam{174,40433,/"40433_GLOBAL_INPUTS.Phase_voltage/", | /"DT_REAL_1/", | Modbusparam{174,40433,/"40433_GLOBAL_INPUTS.Phase_voltage/",/"DT_REAL_1/",},
175 | GLOBAL_INPUTS.Frequency | DT_REAL_1 | MR142 | 40434 | R |  | Modbusparam{175, | 40434,/"40434_GLOBAL_INPUTS.Frequency | Modbusparam{175,40434,/"40434_GLOBAL_INPUTS.Frequency/", | /"DT_REAL_1/", | Modbusparam{175,40434,/"40434_GLOBAL_INPUTS.Frequency/",/"DT_REAL_1/",},
176 | GLOBAL_RUNTIME.Active_alarm | DT_NUMERIC | MW4 | 40435 | R |  | Modbusparam{176, | 40435,/"40435_GLOBAL_RUNTIME.Active_alarm | Modbusparam{176,40435,/"40435_GLOBAL_RUNTIME.Active_alarm/", | /"DT_NUMERIC/", | Modbusparam{176,40435,/"40435_GLOBAL_RUNTIME.Active_alarm/",/"DT_NUMERIC/",},
177 | GLOBAL_RUNTIME.Stopping_alarm | DT_NUMERIC | M39.1 | 40437 | R |  | Modbusparam{177, | 40437,/"40437_GLOBAL_RUNTIME.Stopping_alarm | Modbusparam{177,40437,/"40437_GLOBAL_RUNTIME.Stopping_alarm/", | /"DT_NUMERIC/", | Modbusparam{177,40437,/"40437_GLOBAL_RUNTIME.Stopping_alarm/",/"DT_NUMERIC/",},
178 | GLOBAL_RUNTIME.Cooling_on_alarm | DT_ONOFF | M20.6 | 40438 | R |  | Modbusparam{178, | 40438,/"40438_GLOBAL_RUNTIME.Cooling_on_alarm | Modbusparam{178,40438,/"40438_GLOBAL_RUNTIME.Cooling_on_alarm/", | /"DT_ONOFF/", | Modbusparam{178,40438,/"40438_GLOBAL_RUNTIME.Cooling_on_alarm/",/"DT_ONOFF/",},
179 | GLOBAL_RUNTIME.Stopping_on_alarm | DT_ONOFF | M20.7 | 40439 | R |  | Modbusparam{179, | 40439,/"40439_GLOBAL_RUNTIME.Stopping_on_alarm | Modbusparam{179,40439,/"40439_GLOBAL_RUNTIME.Stopping_on_alarm/", | /"DT_ONOFF/", | Modbusparam{179,40439,/"40439_GLOBAL_RUNTIME.Stopping_on_alarm/",/"DT_ONOFF/",},
180 | GLOBAL_RUNTIME.Start_phase | DT_NUMERIC | MB1880 | 40468 | R |  | Modbusparam{180, | 40468,/"40468_GLOBAL_RUNTIME.Start_phase | Modbusparam{180,40468,/"40468_GLOBAL_RUNTIME.Start_phase/", | /"DT_NUMERIC/", | Modbusparam{180,40468,/"40468_GLOBAL_RUNTIME.Start_phase/",/"DT_NUMERIC/",},
181 | Startmotoreendotermico1.Stop_phase | DT_NUMERIC | MB1879 | 40469 | R |  | Modbusparam{181, | 40469,/"40469_Startmotoreendotermico1.Stop_phase | Modbusparam{181,40469,/"40469_Startmotoreendotermico1.Stop_phase/", | /"DT_NUMERIC/", | Modbusparam{181,40469,/"40469_Startmotoreendotermico1.Stop_phase/",/"DT_NUMERIC/",},
153 | GLOBAL_VARIABLES.Generator_nominal_voltage | DT_REAL_1 | MR1914 | 40473 | R |  | Modbusparam{153, | 40473,/"40473_GLOBAL_VARIABLES.Generator_nominal_voltage | Modbusparam{153,40473,/"40473_GLOBAL_VARIABLES.Generator_nominal_voltage/", | /"DT_REAL_1/", | Modbusparam{153,40473,/"40473_GLOBAL_VARIABLES.Generator_nominal_voltage/",/"DT_REAL_1/",},
154 | GLOBAL_VARIABLES.Generator_nominal_frequency | DT_REAL_1 | MR1918 | 40474 | R |  | Modbusparam{154, | 40474,/"40474_GLOBAL_VARIABLES.Generator_nominal_frequency | Modbusparam{154,40474,/"40474_GLOBAL_VARIABLES.Generator_nominal_frequency/", | /"DT_REAL_1/", | Modbusparam{154,40474,/"40474_GLOBAL_VARIABLES.Generator_nominal_frequency/",/"DT_REAL_1/",},
155 | GLOBAL_VARIABLES.Stop_mode | DT_NUMERIC | MB1882 | 40476 | R |  | Modbusparam{155, | 40476,/"40476_GLOBAL_VARIABLES.Stop_mode | Modbusparam{155,40476,/"40476_GLOBAL_VARIABLES.Stop_mode/", | /"DT_NUMERIC/", | Modbusparam{155,40476,/"40476_GLOBAL_VARIABLES.Stop_mode/",/"DT_NUMERIC/",},
156 | GLOBAL_VARIABLES.Electrovalve_output | DT_NUMERIC | M1872.7 | 40478 | R |  | Modbusparam{156, | 40478,/"40478_GLOBAL_VARIABLES.Electrovalve_output | Modbusparam{156,40478,/"40478_GLOBAL_VARIABLES.Electrovalve_output/", | /"DT_NUMERIC/", | Modbusparam{156,40478,/"40478_GLOBAL_VARIABLES.Electrovalve_output/",/"DT_NUMERIC/",},
157 | GLOBAL_VARIABLES.D+_output | DT_NUMERIC | M30.0 | 40479 | R |  | Modbusparam{157, | 40479,/"40479_GLOBAL_VARIABLES.D+_output | Modbusparam{157,40479,/"40479_GLOBAL_VARIABLES.D+_output/", | /"DT_NUMERIC/", | Modbusparam{157,40479,/"40479_GLOBAL_VARIABLES.D+_output/",/"DT_NUMERIC/",},
158 | AlarmsManger1.In_alarm | DT_NUMERIC | M20.0 | 40480 | R |  | Modbusparam{158, | 40480,/"40480_AlarmsManger1.In_alarm | Modbusparam{158,40480,/"40480_AlarmsManger1.In_alarm/", | /"DT_NUMERIC/", | Modbusparam{158,40480,/"40480_AlarmsManger1.In_alarm/",/"DT_NUMERIC/",},
159 | AlarmsManger1.Siren | DT_NUMERIC | M20.1 | 40481 | R |  | Modbusparam{159, | 40481,/"40481_AlarmsManger1.Siren | Modbusparam{159,40481,/"40481_AlarmsManger1.Siren/", | /"DT_NUMERIC/", | Modbusparam{159,40481,/"40481_AlarmsManger1.Siren/",/"DT_NUMERIC/",},
160 | AlarmsManger1.Global_alarm_#1 | DT_NUMERIC | M20.2 | 40482 | R |  | Modbusparam{160, | 40482,/"40482_AlarmsManger1.Global_alarm_#1 | Modbusparam{160,40482,/"40482_AlarmsManger1.Global_alarm_#1/", | /"DT_NUMERIC/", | Modbusparam{160,40482,/"40482_AlarmsManger1.Global_alarm_#1/",/"DT_NUMERIC/",},
161 | AlarmsManger1.Global_alarm_#2 | DT_NUMERIC | M20.3 | 40483 | R |  | Modbusparam{161, | 40483,/"40483_AlarmsManger1.Global_alarm_#2 | Modbusparam{161,40483,/"40483_AlarmsManger1.Global_alarm_#2/", | /"DT_NUMERIC/", | Modbusparam{161,40483,/"40483_AlarmsManger1.Global_alarm_#2/",/"DT_NUMERIC/",},
162 | AlarmsManger1.Global_alarm_#3 | DT_NUMERIC | M20.4 | 40484 | R |  | Modbusparam{162, | 40484,/"40484_AlarmsManger1.Global_alarm_#3 | Modbusparam{162,40484,/"40484_AlarmsManger1.Global_alarm_#3/", | /"DT_NUMERIC/", | Modbusparam{162,40484,/"40484_AlarmsManger1.Global_alarm_#3/",/"DT_NUMERIC/",},
182 | StartDieselEngine1.Starter_engine_output | DT_NUMERIC | M432.2 | 40540 | R | 88 | Modbusparam{182, | 40540,/"40540_StartDieselEngine1.Starter_engine_output | Modbusparam{182,40540,/"40540_StartDieselEngine1.Starter_engine_output/", | /"DT_NUMERIC/", | Modbusparam{182,40540,/"40540_StartDieselEngine1.Starter_engine_output/",/"DT_NUMERIC/",},
183 | StartDieselEngine1.Pre_heating_output | DT_NUMERIC | M1881.6 | 40543 | R |  | Modbusparam{183, | 40543,/"40543_StartDieselEngine1.Pre_heating_output | Modbusparam{183,40543,/"40543_StartDieselEngine1.Pre_heating_output/", | /"DT_NUMERIC/", | Modbusparam{183,40543,/"40543_StartDieselEngine1.Pre_heating_output/",/"DT_NUMERIC/",},
184 | StartDieselEngine1.IsON | DT_NUMERIC | M1811.3 | 40557 | R |  | Modbusparam{184, | 40557,/"40557_StartDieselEngine1.IsON | Modbusparam{184,40557,/"40557_StartDieselEngine1.IsON/", | /"DT_NUMERIC/", | Modbusparam{184,40557,/"40557_StartDieselEngine1.IsON/",/"DT_NUMERIC/",},
185 | StartDieselEngine1.IsNotStopped | DT_NUMERIC | M1942.1 | 40563 | R |  | Modbusparam{185, | 40563,/"40563_StartDieselEngine1.IsNotStopped | Modbusparam{185,40563,/"40563_StartDieselEngine1.IsNotStopped/", | /"DT_NUMERIC/", | Modbusparam{185,40563,/"40563_StartDieselEngine1.IsNotStopped/",/"DT_NUMERIC/",},
186 | StopDieselEngine1.Electro_magnet_output | DT_NUMERIC | M1942.5 | 40584 | R |  | Modbusparam{186, | 40584,/"40584_StopDieselEngine1.Electro_magnet_output | Modbusparam{186,40584,/"40584_StopDieselEngine1.Electro_magnet_output/", | /"DT_NUMERIC/", | Modbusparam{186,40584,/"40584_StopDieselEngine1.Electro_magnet_output/",/"DT_NUMERIC/",},
187 | GensetManager1.Mains_nominal_voltage | DT_NUMERIC | MW1992 | 40592 | R |  | Modbusparam{187, | 40592,/"40592_GensetManager1.Mains_nominal_voltage | Modbusparam{187,40592,/"40592_GensetManager1.Mains_nominal_voltage/", | /"DT_NUMERIC/", | Modbusparam{187,40592,/"40592_GensetManager1.Mains_nominal_voltage/",/"DT_NUMERIC/",},
188 | GensetManager1.Mains_nominal_frequency | DT_NUMERIC | MB1994 | 40593 | R |  | Modbusparam{188, | 40593,/"40593_GensetManager1.Mains_nominal_frequency | Modbusparam{188,40593,/"40593_GensetManager1.Mains_nominal_frequency/", | /"DT_NUMERIC/", | Modbusparam{188,40593,/"40593_GensetManager1.Mains_nominal_frequency/",/"DT_NUMERIC/",},
189 | GensetManager1.Low_Voltage_mains_(%) | DT_NUMERIC | MB1995 | 40594 | R |  | Modbusparam{189, | 40594,/"40594_GensetManager1.Low_Voltage_mains_(%) | Modbusparam{189,40594,/"40594_GensetManager1.Low_Voltage_mains_(%)/", | /"DT_NUMERIC/", | Modbusparam{189,40594,/"40594_GensetManager1.Low_Voltage_mains_(%)/",/"DT_NUMERIC/",},
190 | GensetManager1.High_Voltage_mains_(%) | DT_NUMERIC | MB1996 | 40595 | R |  | Modbusparam{190, | 40595,/"40595_GensetManager1.High_Voltage_mains_(%) | Modbusparam{190,40595,/"40595_GensetManager1.High_Voltage_mains_(%)/", | /"DT_NUMERIC/", | Modbusparam{190,40595,/"40595_GensetManager1.High_Voltage_mains_(%)/",/"DT_NUMERIC/",},
191 | GensetManager1.Low_Frequency_mains_(%) | DT_NUMERIC_OFF | MB1997 | 40596 | R |  | Modbusparam{191, | 40596,/"40596_GensetManager1.Low_Frequency_mains_(%) | Modbusparam{191,40596,/"40596_GensetManager1.Low_Frequency_mains_(%)/", | /"DT_NUMERIC_OFF/", | Modbusparam{191,40596,/"40596_GensetManager1.Low_Frequency_mains_(%)/",/"DT_NUMERIC_OFF/",},
192 | GensetManager1.High_Frequency_mains_(%) | DT_NUMERIC_OFF | MB1998 | 40597 | R |  | Modbusparam{192, | 40597,/"40597_GensetManager1.High_Frequency_mains_(%) | Modbusparam{192,40597,/"40597_GensetManager1.High_Frequency_mains_(%)/", | /"DT_NUMERIC_OFF/", | Modbusparam{192,40597,/"40597_GensetManager1.High_Frequency_mains_(%)/",/"DT_NUMERIC_OFF/",},
193 | GensetManager1.Low_Voltage_genset_(%) | DT_NUMERIC | MB1999 | 40598 | R |  | Modbusparam{193, | 40598,/"40598_GensetManager1.Low_Voltage_genset_(%) | Modbusparam{193,40598,/"40598_GensetManager1.Low_Voltage_genset_(%)/", | /"DT_NUMERIC/", | Modbusparam{193,40598,/"40598_GensetManager1.Low_Voltage_genset_(%)/",/"DT_NUMERIC/",},
194 | GensetManager1.High_Voltage_genset_(%) | DT_NUMERIC | MB2000 | 40599 | R |  | Modbusparam{194, | 40599,/"40599_GensetManager1.High_Voltage_genset_(%) | Modbusparam{194,40599,/"40599_GensetManager1.High_Voltage_genset_(%)/", | /"DT_NUMERIC/", | Modbusparam{194,40599,/"40599_GensetManager1.High_Voltage_genset_(%)/",/"DT_NUMERIC/",},
195 | GensetManager1.Low_Frequency_genset_(%) | DT_NUMERIC_OFF | MB2001 | 40600 | R |  | Modbusparam{195, | 40600,/"40600_GensetManager1.Low_Frequency_genset_(%) | Modbusparam{195,40600,/"40600_GensetManager1.Low_Frequency_genset_(%)/", | /"DT_NUMERIC_OFF/", | Modbusparam{195,40600,/"40600_GensetManager1.Low_Frequency_genset_(%)/",/"DT_NUMERIC_OFF/",},
196 | GensetManager1.High_Frequency_genset_(%) | DT_NUMERIC_OFF | MB2002 | 40601 | R |  | Modbusparam{196, | 40601,/"40601_GensetManager1.High_Frequency_genset_(%) | Modbusparam{196,40601,/"40601_GensetManager1.High_Frequency_genset_(%)/", | /"DT_NUMERIC_OFF/", | Modbusparam{196,40601,/"40601_GensetManager1.High_Frequency_genset_(%)/",/"DT_NUMERIC_OFF/",},
197 | GensetManager1.Nominal_current_genset | DT_NUMERIC | MW424 | 40606 | R |  | Modbusparam{197, | 40606,/"40606_GensetManager1.Nominal_current_genset | Modbusparam{197,40606,/"40606_GensetManager1.Nominal_current_genset/", | /"DT_NUMERIC/", | Modbusparam{197,40606,/"40606_GensetManager1.Nominal_current_genset/",/"DT_NUMERIC/",},
198 | GensetManager1.Short_circuit_(%) | DT_NUMERIC | MW2010 | 40607 | R |  | Modbusparam{198, | 40607,/"40607_GensetManager1.Short_circuit_(%) | Modbusparam{198,40607,/"40607_GensetManager1.Short_circuit_(%)/", | /"DT_NUMERIC/", | Modbusparam{198,40607,/"40607_GensetManager1.Short_circuit_(%)/",/"DT_NUMERIC/",},
199 | GensetManager1.Current_overload_(%) | DT_NUMERIC | MW2012 | 40608 | R |  | Modbusparam{199, | 40608,/"40608_GensetManager1.Current_overload_(%) | Modbusparam{199,40608,/"40608_GensetManager1.Current_overload_(%)/", | /"DT_NUMERIC/", | Modbusparam{199,40608,/"40608_GensetManager1.Current_overload_(%)/",/"DT_NUMERIC/",},
200 | GensetManager1.mains_OK | DT_ONOFF | M1988.4 | 40624 | R |  | Modbusparam{200, | 40624,/"40624_GensetManager1.mains_OK | Modbusparam{200,40624,/"40624_GensetManager1.mains_OK/", | /"DT_ONOFF/", | Modbusparam{200,40624,/"40624_GensetManager1.mains_OK/",/"DT_ONOFF/",},
201 | GensetManager1.genset_OK | DT_ONOFF | M1988.5 | 40625 | R |  | Modbusparam{201, | 40625,/"40625_GensetManager1.genset_OK | Modbusparam{201,40625,/"40625_GensetManager1.genset_OK/", | /"DT_ONOFF/", | Modbusparam{201,40625,/"40625_GensetManager1.genset_OK/",/"DT_ONOFF/",},
202 | GensetManager1.KWh | DT_NUMERIC | MR2014 | 40627 | R |  | Modbusparam{202, | 40627,/"40627_GensetManager1.KWh | Modbusparam{202,40627,/"40627_GensetManager1.KWh/", | /"DT_NUMERIC/", | Modbusparam{202,40627,/"40627_GensetManager1.KWh/",/"DT_NUMERIC/",},
203 | GensetManager1.KVARh | DT_NUMERIC | MR2018 | 40628 | R |  | Modbusparam{203, | 40628,/"40628_GensetManager1.KVARh | Modbusparam{203,40628,/"40628_GensetManager1.KVARh/", | /"DT_NUMERIC/", | Modbusparam{203,40628,/"40628_GensetManager1.KVARh/",/"DT_NUMERIC/",},
204 | EngineControl1.RPM | DT_NUMERIC | MW2104 | 40655 | R | 104 | Modbusparam{204, | 40655,/"40655_EngineControl1.RPM | Modbusparam{204,40655,/"40655_EngineControl1.RPM/", | /"DT_NUMERIC/", | Modbusparam{204,40655,/"40655_EngineControl1.RPM/",/"DT_NUMERIC/",},
205 | Modbus_MAN_mode | DT_NUMERIC | M7692.1 | 40665 | R/W |  | Modbusparam{205, | 40665,/"40665_Modbus_MAN_mode | Modbusparam{205,40665,/"40665_Modbus_MAN_mode/", | /"DT_NUMERIC/", | Modbusparam{205,40665,/"40665_Modbus_MAN_mode/",/"DT_NUMERIC/",},
206 | Modbus_AUTO_mode | DT_NUMERIC | M7692.2 | 40670 | R/W |  | Modbusparam{206, | 40670,/"40670_Modbus_AUTO_mode | Modbusparam{206,40670,/"40670_Modbus_AUTO_mode/", | /"DT_NUMERIC/", | Modbusparam{206,40670,/"40670_Modbus_AUTO_mode/",/"DT_NUMERIC/",},
207 | Modbus_RESET_mode | DT_NUMERIC | M7692.3 | 40675 | R/W |  | Modbusparam{207, | 40675,/"40675_Modbus_RESET_mode | Modbusparam{207,40675,/"40675_Modbus_RESET_mode/", | /"DT_NUMERIC/", | Modbusparam{207,40675,/"40675_Modbus_RESET_mode/",/"DT_NUMERIC/",},
208 | Modbus_START_mdoe | DT_NUMERIC | M7692.4 | 40680 | R/W |  | Modbusparam{208, | 40680,/"40680_Modbus_START_mdoe | Modbusparam{208,40680,/"40680_Modbus_START_mdoe/", | /"DT_NUMERIC/", | Modbusparam{208,40680,/"40680_Modbus_START_mdoe/",/"DT_NUMERIC/",},
209 | Modbus_STOP_mode | DT_NUMERIC | M7692.5 | 40685 | R/W |  | Modbusparam{209, | 40685,/"40685_Modbus_STOP_mode | Modbusparam{209,40685,/"40685_Modbus_STOP_mode/", | /"DT_NUMERIC/", | Modbusparam{209,40685,/"40685_Modbus_STOP_mode/",/"DT_NUMERIC/",},
210 | Modbus_TEST_mode | DT_NUMERIC | M7692.6 | 40690 | R/W |  | Modbusparam{210, | 40690,/"40690_Modbus_TEST_mode | Modbusparam{210,40690,/"40690_Modbus_TEST_mode/", | /"DT_NUMERIC/", | Modbusparam{210,40690,/"40690_Modbus_TEST_mode/",/"DT_NUMERIC/",},
211 | Modbus_K1_activation | DT_NUMERIC | M7692.7 | 40695 | R/W |  | Modbusparam{211, | 40695,/"40695_Modbus_K1_activation | Modbusparam{211,40695,/"40695_Modbus_K1_activation/", | /"DT_NUMERIC/", | Modbusparam{211,40695,/"40695_Modbus_K1_activation/",/"DT_NUMERIC/",},
212 | Modbus_K2_activation | DT_NUMERIC | M7693.0 | 40700 | R/W |  | Modbusparam{212, | 40700,/"40700_Modbus_K2_activation | Modbusparam{212,40700,/"40700_Modbus_K2_activation/", | /"DT_NUMERIC/", | Modbusparam{212,40700,/"40700_Modbus_K2_activation/",/"DT_NUMERIC/",},
213 | Battery_service_timer | DT_NUMERIC | MW2388 | 40721 | R |  | Modbusparam{213, | 40721,/"40721_Battery_service_timer | Modbusparam{213,40721,/"40721_Battery_service_timer/", | /"DT_NUMERIC/", | Modbusparam{213,40721,/"40721_Battery_service_timer/",/"DT_NUMERIC/",},
214 | K1_output | DT_NUMERIC | M7693.2 | 40746 | R |  | Modbusparam{214, | 40746,/"40746_K1_output | Modbusparam{214,40746,/"40746_K1_output/", | /"DT_NUMERIC/", | Modbusparam{214,40746,/"40746_K1_output/",/"DT_NUMERIC/",},
215 | Test_active | DT_NUMERIC | M2769.3 | 40759 | R |  | Modbusparam{215, | 40759,/"40759_Test_active | Modbusparam{215,40759,/"40759_Test_active/", | /"DT_NUMERIC/", | Modbusparam{215,40759,/"40759_Test_active/",/"DT_NUMERIC/",},
217 | Refueling_pump_output | DT_NUMERIC | M7693.6 | 40951 | R | 802 | Modbusparam{217, | 40951,/"40951_Refueling_pump_output | Modbusparam{217,40951,/"40951_Refueling_pump_output/", | /"DT_NUMERIC/", | Modbusparam{217,40951,/"40951_Refueling_pump_output/",/"DT_NUMERIC/",}, | Особая реализация
218 | Work_hours | DT_NUMERIC | MD3300 | 41109 | R |  | Modbusparam{218, | 41109,/"41109_Work_hours | Modbusparam{218,41109,/"41109_Work_hours/", | /"DT_NUMERIC/", | Modbusparam{218,41109,/"41109_Work_hours/",/"DT_NUMERIC/",},
220 | Service_hours | DT_NUMERIC | MR3340 | 41375 | R |  | Modbusparam{220, | 41375,/"41375_Service_hours | Modbusparam{220,41375,/"41375_Service_hours/", | /"DT_NUMERIC/", | Modbusparam{220,41375,/"41375_Service_hours/",/"DT_NUMERIC/",},
221 | Fuel_litres | DT_NUMERIC | MR3386 | 41395 | R |  | Modbusparam{221, | 41395,/"41395_Fuel_litres | Modbusparam{221,41395,/"41395_Fuel_litres/", | /"DT_NUMERIC/", | Modbusparam{221,41395,/"41395_Fuel_litres/",/"DT_NUMERIC/",},
223 | Autonomy_hours | DT_NUMERIC | MR3404 | 41403 | R |  | Modbusparam{223, | 41403,/"41403_Autonomy_hours | Modbusparam{223,41403,/"41403_Autonomy_hours/", | /"DT_NUMERIC/", | Modbusparam{223,41403,/"41403_Autonomy_hours/",/"DT_NUMERIC/",},
231 | Daily_work_hours | DT_NUMERIC | MR4060 | 41753 | R |  | Modbusparam{231, | 41753,/"41753_Daily_work_hours | Modbusparam{231,41753,/"41753_Daily_work_hours/", | /"DT_NUMERIC/", | Modbusparam{231,41753,/"41753_Daily_work_hours/",/"DT_NUMERIC/",},
232 | Start_counter | DT_NUMERIC | MD4822 | 42171 | R | 1996 | Modbusparam{232, | 42171,/"42171_Start_counter | Modbusparam{232,42171,/"42171_Start_counter/", | /"DT_NUMERIC/", | Modbusparam{232,42171,/"42171_Start_counter/",/"DT_NUMERIC/",},
233 | Engine_warranty | DT_REAL_3 | MR5308 | 42440 | R |  | Modbusparam{233, | 42440,/"42440_Engine_warranty | Modbusparam{233,42440,/"42440_Engine_warranty/", | /"DT_REAL_3/", | Modbusparam{233,42440,/"42440_Engine_warranty/",/"DT_REAL_3/",},
234 | Automatic_set_50Hz | DT_NUMERIC | M7427.4 | 42442 | R/W |  | Modbusparam{234, | 42442,/"42442_Automatic_set_50Hz | Modbusparam{234,42442,/"42442_Automatic_set_50Hz/", | /"DT_NUMERIC/", | Modbusparam{234,42442,/"42442_Automatic_set_50Hz/",/"DT_NUMERIC/",},
235 | Automatic_set_60Hz | DT_NUMERIC | M7427.6 | 42444 | R/W |  | Modbusparam{235, | 42444,/"42444_Automatic_set_60Hz | Modbusparam{235,42444,/"42444_Automatic_set_60Hz/", | /"DT_NUMERIC/", | Modbusparam{235,42444,/"42444_Automatic_set_60Hz/",/"DT_NUMERIC/",},
222 | Instant_consumption | DT_REAL_1 | MR6276 | 43258 | R |  | Modbusparam{222, | 43258,/"43258_Instant_consumption | Modbusparam{222,43258,/"43258_Instant_consumption/", | /"DT_REAL_1/", | Modbusparam{222,43258,/"43258_Instant_consumption/",/"DT_REAL_1/",},
219 | Load_percentage | DT_REAL_1 | MR6280 | 43259 | R |  | Modbusparam{219, | 43259,/"43259_Load_percentage | Modbusparam{219,43259,/"43259_Load_percentage/", | /"DT_REAL_1/", | Modbusparam{219,43259,/"43259_Load_percentage/",/"DT_REAL_1/",},
216 | EJP_-_SCR_active | DT_NUMERIC | M6613.2 | 43480 | R |  | Modbusparam{216, | 43480,/"43480_EJP_-_SCR_active | Modbusparam{216,43480,/"43480_EJP_-_SCR_active/", | /"DT_NUMERIC/", | Modbusparam{216,43480,/"43480_EJP_-_SCR_active/",/"DT_NUMERIC/",},
227 | Dummy_load_output | DT_NUMERIC | M6612.3 | 43505 | R |  | Modbusparam{227, | 43505,/"43505_Dummy_load_output | Modbusparam{227,43505,/"43505_Dummy_load_output/", | /"DT_NUMERIC/", | Modbusparam{227,43505,/"43505_Dummy_load_output/",/"DT_NUMERIC/",},
229 | Last_refilling | DT_NUMERIC | MW7050 | 43812 | R |  | Modbusparam{229, | 43812,/"43812_Last_refilling | Modbusparam{229,43812,/"43812_Last_refilling/", | /"DT_NUMERIC/", | Modbusparam{229,43812,/"43812_Last_refilling/",/"DT_NUMERIC/",},
226 | Delta_fuel | DT_REAL_1 | MR7060 | 43815 | R |  | Modbusparam{226, | 43815,/"43815_Delta_fuel | Modbusparam{226,43815,/"43815_Delta_fuel/", | /"DT_REAL_1/", | Modbusparam{226,43815,/"43815_Delta_fuel/",/"DT_REAL_1/",},
228 | Total_opex_cost | DT_REAL_1 | MR7080 | 43820 | R |  | Modbusparam{228, | 43820,/"43820_Total_opex_cost | Modbusparam{228,43820,/"43820_Total_opex_cost/", | /"DT_REAL_1/", | Modbusparam{228,43820,/"43820_Total_opex_cost/",/"DT_REAL_1/",},
230 | Lost_Refilling | DT_NUMERIC | MR7526 | 44158 | R |  | Modbusparam{230, | 44158,/"44158_Lost_Refilling | Modbusparam{230,44158,/"44158_Lost_Refilling/", | /"DT_NUMERIC/", | Modbusparam{230,44158,/"44158_Lost_Refilling/",/"DT_NUMERIC/",},
225 | Work_interval_hours | DT_REAL_1 | MR7560 | 44166 | R |  | Modbusparam{225, | 44166,/"44166_Work_interval_hours | Modbusparam{225,44166,/"44166_Work_interval_hours/", | /"DT_REAL_1/", | Modbusparam{225,44166,/"44166_Work_interval_hours/",/"DT_REAL_1/",},
224 | Work_interval_consumption | DT_REAL_1 | MR7564 | 44167 | R |  | Modbusparam{224, | 44167,/"44167_Work_interval_consumption | Modbusparam{224,44167,/"44167_Work_interval_consumption/", | /"DT_REAL_1/", | Modbusparam{224,44167,/"44167_Work_interval_consumption/",/"DT_REAL_1/",},

## Sheet1
1 | GLOBALS.Focus | DT_NUMERIC | MB1 | 40002 | R | 0
|  |  |  | 40003 |  | 1
2 | GLOBALS.Program | DT_NUMERIC | MB3 | 40004 | R | 2
|  |  |  | 40005 |  | 3
|  |  |  | 40006 |  | 4
|  |  |  | 40007 |  | 5
|  |  |  | 40008 |  | 6
|  |  |  | 40009 |  | 7
|  |  |  | 40010 |  | 8
|  |  |  | 40011 |  | 9
|  |  |  | 40012 |  | 10
|  |  |  | 40013 |  | 11
|  |  |  | 40014 |  | 12
|  |  |  | 40015 |  | 13
|  |  |  | 40016 |  | 14
|  |  |  | 40017 |  | 15
|  |  |  | 40018 |  | 16
|  |  |  | 40019 |  | 17
|  |  |  | 40020 |  | 18
|  |  |  | 40021 |  | 19
|  |  |  | 40022 |  | 20
|  |  |  | 40023 |  | 21
|  |  |  | 40024 |  | 22
|  |  |  | 40025 |  | 23
|  |  |  | 40026 |  | 24
|  |  |  | 40027 |  | 25
|  |  |  | 40028 |  | 26
|  |  |  | 40029 |  | 27
|  |  |  | 40030 |  | 28
|  |  |  | 40031 |  | 29
|  |  |  | 40032 |  | 30
|  |  |  | 40033 |  | 31
|  |  |  | 40034 |  | 32
3 | GLOBALS.Year | DT_NUMERIC | MB210 | 40035 | R | 33
4 | GLOBALS.Month | DT_NUMERIC | MB211 | 40036 | R | 34
5 | GLOBALS.Day | DT_NUMERIC | MB212 | 40037 | R | 35
6 | GLOBALS.Hour | DT_NUMERIC | MB213 | 40038 | R | 36
7 | GLOBALS.Minute | DT_NUMERIC | MB214 | 40039 | R | 37
8 | GLOBALS.Second | DT_NUMERIC | MB215 | 40040 | R | 38
|  |  |  | 40041 |  | 39
9 | GLOBALS.Day_of_the_week | DT_NUMERIC | MB216 | 40042 | R | 40
10 | GLOBALS.Modem_Status | DT_NUMERIC | MB218 | 40043 | R | 41

## Sheet2
106 | RID1000A_BOARD.COM_protocol | DT_SERIAL_PROTOCOLS_RID | MB250 | 40050 | R | 0
107 | RID1000A_BOARD.Baud_rate_COM | DT_SERIAL_BAUDRATE | MB251 | 40051 | R | 1
|  |  |  | 40052 |  | 2
|  |  |  | 40053 |  | 3
|  |  |  | 40054 |  | 4
108 | RID1000A_BOARD.RS485_protocol | DT_SERIAL_PROTOCOLS_RID | MB255 | 40055 | R | 5
109 | RID1000A_BOARD.Baud_rate_RS485 | DT_SERIAL_BAUDRATE | MB256 | 40056 | R | 6
|  |  |  | 40057 |  | 7
|  |  |  | 40058 |  | 8
|  |  |  | 40059 |  | 9
110 | RID1000A_BOARD.Bit_rates | DT_CAN_BITRATES | MB267 | 40060 | R | 10
111 | RID1000A_BOARD.CAN_protocol | DT_CAN_PROTOCOLS | MB268 | 40061 | R | 11
112 | RID1000A_BOARD.Address | DT_NUMERIC | MB260 | 40062 | R | 12
113 | RID1000A_BOARD.Centre_SMS | DT_STRING | MW270 | 40063 | R | 13
114 | RID1000A_BOARD.SMS_1_number | DT_STRING | MW272 | 40064 | R | 14
115 | RID1000A_BOARD.SMS_2_number | DT_STRING | MW274 | 40065 | R | 15
116 | RID1000A_BOARD.SMS_3_number | DT_STRING | MW276 | 40066 | R | 16
117 | RID1000A_BOARD.SMS_4_number | DT_STRING | MW278 | 40067 | R | 17
118 | RID1000A_BOARD.SMS_5_number | DT_STRING | MW280 | 40068 | R | 18
119 | RID1000A_BOARD.Sampling_time | DT_NUMERIC | MW430 | 40069 | R | 19
|  |  |  | 40070 |  | 20
120 | RID1000A_BOARD.Datalogger_Enable | DT_NUMERIC_OFF | M432.1 | 40071 | R | 21
|  |  |  | 40072 |  | 22
|  |  |  | 40073 |  | 23
|  |  |  | 40074 |  | 24
|  |  |  | 40075 |  | 25
|  |  |  | 40076 |  | 26
121 | RID1000A_BOARD.Upload_data_SMS | DT_STRING | MW586 | 40077 | R | 27
122 | RID1000A_BOARD.Upload_adta_apn | DT_STRING | MW588 | 40078 | R | 28
123 | RID1000A_BOARD.Upload_data_server | DT_STRING | MW590 | 40079 | R | 29
124 | RID1000A_BOARD.Upload_data_service | DT_STRING | MW592 | 40080 | R | 30
125 | RID1000A_BOARD.Server_port | DT_NUMERIC | MW594 | 40081 | R | 31
126 | RID1000A_BOARD.Upload_interval | DT_NUMERIC | MW596 | 40082 | R | 32
127 | RID1000A_BOARD.Upload_type | DT_UPLOAD_TYPE | MB598 | 40083 | R | 33
128 | RID1000A_BOARD.ID_Upload | DT_NUMERIC_OFF | MW146 | 40084 | R | 34
129 | RID1000A_BOARD.Input_type_1 | DT_DIO_TYPES | MB535 | 40085 | R | 35
130 | RID1000A_BOARD.Input_type_2 | DT_DIO_TYPES | MB536 | 40086 | R | 36
131 | RID1000A_BOARD.Input_type_3 | DT_DIO_TYPES | MB537 | 40087 | R | 37
132 | RID1000A_BOARD.Input_type_4 | DT_DIO_TYPES | MB538 | 40088 | R | 38
133 | RID1000A_BOARD.Input_type_5 | DT_DIO_TYPES | MB539 | 40089 | R | 39
134 | RID1000A_BOARD.Emergency_input_type | DT_DIO_TYPES | MB585 | 40090 | R | 40
135 | RID1000A_BOARD.Output_type_EV | DT_DIO_TYPES | MB540 | 40091 | R | 41
136 | RID1000A_BOARD.Output_type_AVV | DT_DIO_TYPES | MB541 | 40092 | R | 42
137 | RID1000A_BOARD.Output_type_1 | DT_DIO_TYPES | MB542 | 40093 | R | 43
138 | RID1000A_BOARD.Output_type_2 | DT_DIO_TYPES | MB543 | 40094 | R | 44
139 | RID1000A_BOARD.Output_type_3 | DT_DIO_TYPES | MB544 | 40095 | R | 45
140 | RID1000A_BOARD.Output_type_4 | DT_DIO_TYPES | MB545 | 40096 | R | 46
141 | RID1000A_BOARD.Analog_type_1 | DT_ANI_TYPES | MB546 | 40097 | R | 47
142 | RID1000A_BOARD.Analog_type_2 | DT_ANI_TYPES | MB547 | 40098 | R | 48
143 | RID1000A_BOARD.Analog_type_3 | DT_ANI_TYPES | MB548 | 40099 | R | 49
144 | RID1000A_BOARD.Offset_VRR | DT_NUMERIC | MR549 | 40100 | R | 50
145 | RID1000A_BOARD.Offset_VRS | DT_NUMERIC | MR553 | 40101 | R | 51
146 | RID1000A_BOARD.Offset_VRT | DT_NUMERIC | MR557 | 40102 | R | 52
147 | RID1000A_BOARD.Offset_VGR | DT_NUMERIC | MR561 | 40103 | R | 53
148 | RID1000A_BOARD.Offset_VGS | DT_NUMERIC | MR565 | 40104 | R | 54
149 | RID1000A_BOARD.Offset_VGT | DT_NUMERIC | MR569 | 40105 | R | 55
150 | RID1000A_BOARD.Offset_IR | DT_REAL_1 | MR573 | 40106 | R | 56
151 | RID1000A_BOARD.Offset_IS | DT_REAL_1 | MR577 | 40107 | R | 57
152 | RID1000A_BOARD.Offset_IT | DT_REAL_1 | MR581 | 40108 | R | 58

## Sheet3
11 | RID1000A_BOARD.Input_J4.8 | DT_ONOFF | I0.0 | 40134 | R | 0
12 | RID1000A_BOARD.Input_J4.7 | DT_ONOFF | I0.1 | 40135 | R | 1
13 | RID1000A_BOARD.Input_J4.6 | DT_ONOFF | I0.2 | 40136 | R | 2
14 | RID1000A_BOARD.Input_J4.5 | DT_ONOFF | I0.3 | 40137 | R | 3
15 | RID1000A_BOARD.Input_J4.4 | DT_ONOFF | I0.4 | 40138 | R | 4
16 | RID1000A_BOARD.Oil_pressure | DT_REAL_1 | IR2 | 40139 | R | 5
17 | RID1000A_BOARD.Water_temperature | DT_REAL_1 | IR6 | 40140 | R | 6
18 | RID1000A_BOARD.Fuel_level | DT_NUMERIC | IR10 | 40141 | R | 7
19 | RID1000A_BOARD.Battery_voltage | DT_REAL_1 | IR14 | 40142 | R | 8
20 | RID1000A_BOARD.Line_R_voltage_mains | DT_NUMERIC | IR18 | 40143 | R | 9
21 | RID1000A_BOARD.Line_S_voltage_mains | DT_NUMERIC | IR22 | 40144 | R | 10
22 | RID1000A_BOARD.Line_T_voltage_mains | DT_NUMERIC | IR26 | 40145 | R | 11
23 | RID1000A_BOARD.Line_R_voltage_genset | DT_NUMERIC | IR30 | 40146 | R | 12
24 | RID1000A_BOARD.Line_S_voltage_genset | DT_NUMERIC | IR34 | 40147 | R | 13
25 | RID1000A_BOARD.Line_T_voltage_genset | DT_NUMERIC | IR38 | 40148 | R | 14
26 | RID1000A_BOARD.Load_currente_phase_R | DT_NUMERIC | IR42 | 40149 | R | 15
27 | RID1000A_BOARD.Load_current_phase_S | DT_NUMERIC | IR46 | 40150 | R | 16
28 | RID1000A_BOARD.Load_current_phase_T | DT_NUMERIC | IR50 | 40151 | R | 17
29 | RID1000A_BOARD.Frequency_mains | DT_REAL_1 | IR54 | 40152 | R | 18
30 | RID1000A_BOARD.Frequency_genset | DT_REAL_1 | IR58 | 40153 | R | 19
31 | RID1000A_BOARD.Active_power_phase_R | DT_REAL_1 | IR62 | 40154 | R | 20
32 | RID1000A_BOARD.Active_power_phase_S | DT_REAL_1 | IR66 | 40155 | R | 21
33 | RID1000A_BOARD.Active_power_phase_T | DT_REAL_1 | IR70 | 40156 | R | 22
34 | RID1000A_BOARD.Phase_voltage_mains | DT_REAL_1 | IR74 | 40157 | R | 23
35 | RID1000A_BOARD.Phase_voltage_genset | DT_REAL_1 | IR78 | 40158 | R | 24
36 | RID1000A_BOARD.Apparent_power_phase_R | DT_REAL_1 | IR82 | 40159 | R | 25
37 | RID1000A_BOARD.Apparent_power_phase_S | DT_REAL_1 | IR86 | 40160 | R | 26
38 | RID1000A_BOARD.Apparent_power_phase_T | DT_REAL_1 | IR90 | 40161 | R | 27
39 | RID1000A_BOARD.Reactive_power_phase_R | DT_REAL_1 | IR94 | 40162 | R | 28
40 | RID1000A_BOARD.Reactive_power_phase_S | DT_REAL_1 | IR98 | 40163 | R | 29
41 | RID1000A_BOARD.Reactive_power_phase_T | DT_REAL_1 | IR102 | 40164 | R | 30
42 | RID1000A_BOARD.Reactive_power_totale | DT_REAL_1 | IR106 | 40165 | R | 31
43 | RID1000A_BOARD.Power_factor_phase_R | DT_REAL_2 | IR110 | 40166 | R | 32
44 | RID1000A_BOARD.Power_factor_phase_S | DT_REAL_2 | IR114 | 40167 | R | 33
45 | RID1000A_BOARD.Power_factor_phase_T | DT_REAL_2 | IR118 | 40168 | R | 34
46 | RID1000A_BOARD.Wrong_phase_sequence_mains | DT_ONOFF | I0.5 | 40169 | R | 35
47 | RID1000A_BOARD.Wrong_phase_sequence_genset | DT_ONOFF | I0.6 | 40170 | R | 36
48 | RID1000A_BOARD.Emergency | DT_ONOFF | I0.7 | 40171 | R | 37
49 | RID1000A_BOARD.Total_apparent_power | DT_REAL_1 | IR122 | 40174 | R | 38
50 | RID1000A_BOARD.Total_active_power | DT_REAL_1 | IR126 | 40175 | R | 39
51 | RID1000A_BOARD.Total_power_factor | DT_REAL_2 | IR130 | 40176 | R | 40
52 | RID1000A_BOARD.Higher_consumption_current | DT_REAL_1 | IR134 | 40177 | R | 41
53 | RID1000A_BOARD.Frequency_PICKUP_(Hz) | DT_NUMERIC | IR138 | 40178 | R | 42
54 | RID1000A_BOARD.Voltage_D+ | DT_REAL_1 | IR142 | 40179 | R | 43
55 | RID1000A_BOARD.Phase_voltage_R-S_mains | DT_NUMERIC | IR146 | 40180 | R | 44
56 | RID1000A_BOARD.Phase_voltage_S-T_mains | DT_NUMERIC | IR150 | 40181 | R | 45
57 | RID1000A_BOARD.Phase_voltage_T-R_mains | DT_NUMERIC | IR154 | 40182 | R | 46
58 | RID1000A_BOARD.Phase_voltage_R-S_genset | DT_NUMERIC | IR158 | 40183 | R | 47
59 | RID1000A_BOARD.Phase_voltage_S-T_genset | DT_NUMERIC | IR162 | 40184 | R | 48
60 | RID1000A_BOARD.Phase_voltage_T-R_genset | DT_NUMERIC | IR166 | 40185 | R | 49
61 | RID1000A_BOARD.Rpm_(SPN_190) | DT_NUMERIC | IR300 | 40186 | R | 50
62 | RID1000A_BOARD.Oil_pressure_(SPN_100) | DT_REAL_1 | IR304 | 40187 | R | 51
63 | RID1000A_BOARD.Engine_temperature_(SPN_110) | DT_REAL_1 | IR308 | 40188 | R | 52
64 | RID1000A_BOARD.Fuel_temperature_(SPN_174) | DT_REAL_1 | IR312 | 40189 | R | 53
65 | RID1000A_BOARD.Oil_temperature_(SPN_175) | DT_REAL_1 | IR316 | 40190 | R | 54
66 | RID1000A_BOARD.Fuel_pressure_(SPN_094) | DT_REAL_1 | IR320 | 40191 | R | 55
67 | RID1000A_BOARD.Oil_level_(SPN_098) | DT_REAL_1 | IR324 | 40192 | R | 56
68 | RID1000A_BOARD.Carter_pressure_(SPN_101) | DT_REAL_1 | IR328 | 40193 | R | 57
69 | RID1000A_BOARD.Coolant_pressure_(SPN_109) | DT_REAL_1 | IR332 | 40194 | R | 58
70 | RID1000A_BOARD.Coolant_level_(SPN_111) | DT_REAL_1 | IR336 | 40195 | R | 59
71 | RID1000A_BOARD.Total_work_hours_(SPN_247) | DT_NUMERIC | IR340 | 40196 | R | 60
72 | RID1000A_BOARD.Turbo_pressure_(SPN_102) | DT_REAL_1 | IR344 | 40197 | R | 61
73 | RID1000A_BOARD.Turbo_temeprature_(SPN_105) | DT_NUMERIC | IR348 | 40198 | R | 62
74 | RID1000A_BOARD.Instant_consumption_(SPN_183) | DT_REAL_1 | IR352 | 40199 | R | 63
75 | RID1000A_BOARD.Torque_(SPN_513) | DT_NUMERIC | IR356 | 40200 | R | 64
76 | RID1000A_BOARD.Torque_request_(SPN_512) | DT_NUMERIC | IR360 | 40201 | R | 65
77 | RID1000A_BOARD.Water_level_(SPN_97) | DT_NUMERIC | IR364 | 40202 | R | 66
78 | RID1000A_BOARD.Accelerator_position_(%)_(SPN_91) | DT_NUMERIC | IR368 | 40203 | R | 67
79 | RID1000A_BOARD.Load_percentage_(SPN_92) | DT_NUMERIC | IR372 | 40204 | R | 68
80 | RID1000A_BOARD.Battery_voltage_(SPN_158) | DT_REAL_1 | IR376 | 40205 | R | 69
81 | RID1000A_BOARD.Aspiration_pressure_(SPN_106) | DT_REAL_1 | IR380 | 40206 | R | 70
82 | RID1000A_BOARD.Atmospheric_pressure_(SPN_108) | DT_REAL_1 | IR384 | 40207 | R | 71
83 | RID1000A_BOARD.Discharge_temperature_(SPN_173) | DT_REAL_1 | IR388 | 40208 | R | 72
84 | RID1000A_BOARD.DTC_-_SPN | DT_NUMERIC | IR392 | 40209 | R | 73
85 | RID1000A_BOARD.DTC_-_FMI | DT_NUMERIC | IR396 | 40210 | R | 74
|  |  |  | 40211 |  | 75
|  |  |  | 40212 |  | 76
|  |  |  | 40213 |  | 77
|  |  |  | 40214 |  | 78
86 | RID1000A_BOARD.Start_output | DT_ONOFF | U0.0 | 40215 | R | 79
87 | RID1000A_BOARD.EV_output | DT_ONOFF | U0.1 | 40216 | R | 80
88 | RID1000A_BOARD.Genset_contactor | DT_ONOFF | U0.2 | 40217 | R | 81
89 | RID1000A_BOARD.Mains_contactor | DT_ONOFF | U0.3 | 40218 | R | 82
90 | RID1000A_BOARD.Excitation | DT_ONOFF | U0.4 | 40219 | R | 83
91 | RID1000A_BOARD.Out_J5.11 | DT_ONOFF | U1.0 | 40220 | R | 84
92 | RID1000A_BOARD.Out_J5.10 | DT_ONOFF | U1.1 | 40221 | R | 85
93 | RID1000A_BOARD.Out_J5.9 | DT_ONOFF | U1.2 | 40222 | R | 86
94 | RID1000A_BOARD.Out_J5.8 | DT_ONOFF | U1.3 | 40223 | R | 87
95 | RID1000A_BOARD.Led_ON/OFF | DT_ONOFF | U2.0 | 40224 | R | 88
96 | RID1000A_BOARD.Led_KG1 | DT_ONOFF | U2.1 | 40225 | R | 89
97 | RID1000A_BOARD.Led_RES | DT_ONOFF | U2.2 | 40226 | R | 90
98 | RID1000A_BOARD.Led_AUT | DT_ONOFF | U2.3 | 40227 | R | 91
99 | RID1000A_BOARD.Led_KR | DT_ONOFF | U2.4 | 40228 | R | 92
100 | RID1000A_BOARD.Led_KR1 | DT_ONOFF | U2.5 | 40229 | R | 93
101 | RID1000A_BOARD.Led_KG | DT_ONOFF | U2.6 | 40230 | R | 94
102 | RID1000A_BOARD.Led_TEST | DT_ONOFF | U2.7 | 40231 | R | 95
103 | RID1000A_BOARD.Led_MAN | DT_ONOFF | U3.0 | 40232 | R | 96
104 | RID1000A_BOARD.Led_ALARM | DT_ONOFF | U3.1 | 40233 | R | 97
|  |  |  | 40234 |  | 98
|  |  |  | 40235 |  | 99
105 | RID1000A_BOARD.Full_memory | DT_ONOFF | I500.0 | 40236 | R | 100

## Sheet4
163 | GLOBAL_INPUTS.Engine_temperature | DT_REAL_1 | MR102 | 40422 | R | 0
164 | GLOBAL_INPUTS.Digital_engine_temperature | DT_ONOFF | M100.0 | 40423 | R | 1
165 | GLOBAL_INPUTS.Input_D+ | DT_REAL_1 | MR114 | 40424 | R | 2
166 | GLOBAL_INPUTS.Input_Pick_up | DT_REAL_1 | MR118 | 40425 | R | 3
167 | GLOBAL_INPUTS.Input_SAPRISA | DT_REAL_1 | MR122 | 40426 | R | 4
168 | GLOBAL_INPUTS.Input_W | DT_REAL_1 | MR126 | 40427 | R | 5
169 | GLOBAL_INPUTS.Oil_pressure | DT_REAL_1 | MR110 | 40428 | R | 6
170 | GLOBAL_INPUTS.Digital_oil_pressure | DT_ONOFF | M100.2 | 40429 | R | 7
171 | GLOBAL_INPUTS.Fuel_level_(%) | DT_REAL_1 | MR106 | 40430 | R | 8
172 | GLOBAL_INPUTS.Low_fuel_level_digital | DT_ONOFF | M100.1 | 40431 | R | 9
173 | GLOBAL_INPUTS.Battery_voltage | DT_REAL_1 | MR130 | 40432 | R | 10
174 | GLOBAL_INPUTS.Phase_voltage | DT_REAL_1 | MR138 | 40433 | R | 11
175 | GLOBAL_INPUTS.Frequency | DT_REAL_1 | MR142 | 40434 | R | 12
176 | GLOBAL_RUNTIME.Active_alarm | DT_NUMERIC | MW4 | 40435 | R | 13
177 | GLOBAL_RUNTIME.Stopping_alarm | DT_NUMERIC | M39.1 | 40437 | R | 14
178 | GLOBAL_RUNTIME.Cooling_on_alarm | DT_ONOFF | M20.6 | 40438 | R | 15
179 | GLOBAL_RUNTIME.Stopping_on_alarm | DT_ONOFF | M20.7 | 40439 | R | 16 | 28
|  |  |  | 40440 |  | 17
|  |  |  | 40441 |  | 18
|  |  |  | 40442 |  | 19
|  |  |  | 40443 |  | 20
|  |  |  | 40444 |  | 21
|  |  |  | 40445 |  | 22
|  |  |  | 40446 |  | 23
|  |  |  | 40447 |  | 24
|  |  |  | 40448 |  | 25
|  |  |  | 40449 |  | 26
|  |  |  | 40450 |  | 27
|  |  |  | 40451 |  | 28
|  |  |  | 40452 |  | 29
|  |  |  | 40453 |  | 30
|  |  |  | 40454 |  | 31
|  |  |  | 40455 |  | 32
|  |  |  | 40456 |  | 33
|  |  |  | 40457 |  | 34
|  |  |  | 40458 |  | 35
|  |  |  | 40459 |  | 36
|  |  |  | 40460 |  | 37
|  |  |  | 40461 |  | 38
|  |  |  | 40462 |  | 39
|  |  |  | 40463 |  | 40
|  |  |  | 40464 |  | 41
|  |  |  | 40465 |  | 42
|  |  |  | 40466 |  | 43
|  |  |  | 40467 |  | 44
180 | GLOBAL_RUNTIME.Start_phase | DT_NUMERIC | MB1880 | 40468 | R | 45
181 | Startmotoreendotermico1.Stop_phase | DT_NUMERIC | MB1879 | 40469 | R | 46
|  |  |  | 40470 |  | 47
|  |  |  | 40471 |  | 48
|  |  |  | 40472 |  | 49
153 | GLOBAL_VARIABLES.Generator_nominal_voltage | DT_REAL_1 | MR1914 | 40473 | R | 50
154 | GLOBAL_VARIABLES.Generator_nominal_frequency | DT_REAL_1 | MR1918 | 40474 | R | 51
|  |  |  | 40475 |  | 52
155 | GLOBAL_VARIABLES.Stop_mode | DT_NUMERIC | MB1882 | 40476 | R | 53
|  |  |  | 40477 |  | 54
156 | GLOBAL_VARIABLES.Electrovalve_output | DT_NUMERIC | M1872.7 | 40478 | R | 55
157 | GLOBAL_VARIABLES.D+_output | DT_NUMERIC | M30.0 | 40479 | R | 56
158 | AlarmsManger1.In_alarm | DT_NUMERIC | M20.0 | 40480 | R | 57
159 | AlarmsManger1.Siren | DT_NUMERIC | M20.1 | 40481 | R | 58
160 | AlarmsManger1.Global_alarm_#1 | DT_NUMERIC | M20.2 | 40482 | R | 59
161 | AlarmsManger1.Global_alarm_#2 | DT_NUMERIC | M20.3 | 40483 | R | 60
162 | AlarmsManger1.Global_alarm_#3 | DT_NUMERIC | M20.4 | 40484 | R | 61

## Sheet5
182 | StartDieselEngine1.Starter_engine_output | DT_NUMERIC | M432.2 | 40540 | R | 0
|  |  |  | 40541 |  | 1
|  |  |  | 40542 |  | 2
183 | StartDieselEngine1.Pre_heating_output | DT_NUMERIC | M1881.6 | 40543 | R | 3
|  |  |  | 40544 |  | 4
|  |  |  | 40545 |  | 5
|  |  |  | 40546 |  | 6
|  |  |  | 40547 |  | 7
|  |  |  | 40548 |  | 8
|  |  |  | 40549 |  | 9
|  |  |  | 40550 |  | 10
|  |  |  | 40551 |  | 11
|  |  |  | 40552 |  | 12
|  |  |  | 40553 |  | 13
|  |  |  | 40554 |  | 14
|  |  |  | 40555 |  | 15
|  |  |  | 40556 |  | 16
184 | StartDieselEngine1.IsON | DT_NUMERIC | M1811.3 | 40557 | R | 17
|  |  |  | 40558 |  | 18
|  |  |  | 40559 |  | 19
|  |  |  | 40560 |  | 20
|  |  |  | 40561 |  | 21
|  |  |  | 40562 |  | 22
185 | StartDieselEngine1.IsNotStopped | DT_NUMERIC | M1942.1 | 40563 | R | 23 | 20
|  |  |  | 40564 |  | 24
|  |  |  | 40565 |  | 25
|  |  |  | 40566 |  | 26
|  |  |  | 40567 |  | 27
|  |  |  | 40568 |  | 28
|  |  |  | 40569 |  | 29
|  |  |  | 40570 |  | 30
|  |  |  | 40571 |  | 31
|  |  |  | 40572 |  | 32
|  |  |  | 40573 |  | 33
|  |  |  | 40574 |  | 34
|  |  |  | 40575 |  | 35
|  |  |  | 40576 |  | 36
|  |  |  | 40577 |  | 37
|  |  |  | 40578 |  | 38
|  |  |  | 40579 |  | 39
|  |  |  | 40580 |  | 40
|  |  |  | 40581 |  | 41
|  |  |  | 40582 |  | 42
|  |  |  | 40583 |  | 43
186 | StopDieselEngine1.Electro_magnet_output | DT_NUMERIC | M1942.5 | 40584 | R | 44
|  |  |  | 40585 |  | 45
|  |  |  | 40586 |  | 46
|  |  |  | 40587 |  | 47
|  |  |  | 40588 |  | 48
|  |  |  | 40589 |  | 49
|  |  |  | 40590 |  | 50
|  |  |  | 40591 |  | 51
187 | GensetManager1.Mains_nominal_voltage | DT_NUMERIC | MW1992 | 40592 | R | 52
188 | GensetManager1.Mains_nominal_frequency | DT_NUMERIC | MB1994 | 40593 | R | 53
189 | GensetManager1.Low_Voltage_mains_(%) | DT_NUMERIC | MB1995 | 40594 | R | 54
190 | GensetManager1.High_Voltage_mains_(%) | DT_NUMERIC | MB1996 | 40595 | R | 55
191 | GensetManager1.Low_Frequency_mains_(%) | DT_NUMERIC_OFF | MB1997 | 40596 | R | 56
192 | GensetManager1.High_Frequency_mains_(%) | DT_NUMERIC_OFF | MB1998 | 40597 | R | 57
193 | GensetManager1.Low_Voltage_genset_(%) | DT_NUMERIC | MB1999 | 40598 | R | 58
194 | GensetManager1.High_Voltage_genset_(%) | DT_NUMERIC | MB2000 | 40599 | R | 59
195 | GensetManager1.Low_Frequency_genset_(%) | DT_NUMERIC_OFF | MB2001 | 40600 | R | 60
196 | GensetManager1.High_Frequency_genset_(%) | DT_NUMERIC_OFF | MB2002 | 40601 | R | 61
|  |  |  | 40602 |  | 62
|  |  |  | 40603 |  | 63
|  |  |  | 40604 |  | 64
|  |  |  | 40605 |  | 65
197 | GensetManager1.Nominal_current_genset | DT_NUMERIC | MW424 | 40606 | R | 66
198 | GensetManager1.Short_circuit_(%) | DT_NUMERIC | MW2010 | 40607 | R | 67
199 | GensetManager1.Current_overload_(%) | DT_NUMERIC | MW2012 | 40608 | R | 68
|  |  |  | 40609 |  | 69
|  |  |  | 40610 |  | 70
|  |  |  | 40611 |  | 71
|  |  |  | 40612 |  | 72
|  |  |  | 40613 |  | 73
|  |  |  | 40614 |  | 74
|  |  |  | 40615 |  | 75
|  |  |  | 40616 |  | 76
|  |  |  | 40617 |  | 77
|  |  |  | 40618 |  | 78
|  |  |  | 40619 |  | 79
|  |  |  | 40620 |  | 80
|  |  |  | 40621 |  | 81
|  |  |  | 40622 |  | 82
|  |  |  | 40623 |  | 83
200 | GensetManager1.mains_OK | DT_ONOFF | M1988.4 | 40624 | R | 84
201 | GensetManager1.genset_OK | DT_ONOFF | M1988.5 | 40625 | R | 85
|  |  |  | 40626 |  | 86
202 | GensetManager1.KWh | DT_NUMERIC | MR2014 | 40627 | R | 87
203 | GensetManager1.KVARh | DT_NUMERIC | MR2018 | 40628 | R | 88

## Sheet6
204 | EngineControl1.RPM | DT_NUMERIC | MW2104 | 40655 | R | 0
|  |  |  | 40656 |  | 1
|  |  |  | 40657 |  | 2
|  |  |  | 40658 |  | 3
|  |  |  | 40659 |  | 4
|  |  |  | 40660 |  | 5
|  |  |  | 40661 |  | 6
|  |  |  | 40662 |  | 7
|  |  |  | 40663 |  | 8
|  |  |  | 40664 |  | 9
205 | Modbus_MAN_mode | DT_NUMERIC | M7692.1 | 40665 | R/W | 10
|  |  |  | 40666 |  | 11
|  |  |  | 40667 |  | 12
|  |  |  | 40668 |  | 13
|  |  |  | 40669 |  | 14
206 | Modbus_AUTO_mode | DT_NUMERIC | M7692.2 | 40670 | R/W | 15
|  |  |  | 40671 |  | 16
|  |  |  | 40672 |  | 17
|  |  |  | 40673 |  | 18
|  |  |  | 40674 |  | 19
207 | Modbus_RESET_mode | DT_NUMERIC | M7692.3 | 40675 | R/W | 20
|  |  |  | 40676 |  | 21
|  |  |  | 40677 |  | 22
|  |  |  | 40678 |  | 23
|  |  |  | 40679 |  | 24
208 | Modbus_START_mdoe | DT_NUMERIC | M7692.4 | 40680 | R/W | 25
|  |  |  | 40681 |  | 26
|  |  |  | 40682 |  | 27
|  |  |  | 40683 |  | 28
|  |  |  | 40684 |  | 29
209 | Modbus_STOP_mode | DT_NUMERIC | M7692.5 | 40685 | R/W | 30
|  |  |  | 40686 |  | 31
|  |  |  | 40687 |  | 32
|  |  |  | 40688 |  | 33
|  |  |  | 40689 |  | 34
210 | Modbus_TEST_mode | DT_NUMERIC | M7692.6 | 40690 | R/W | 35
|  |  |  | 40691 |  | 36
|  |  |  | 40692 |  | 37
|  |  |  | 40693 |  | 38
|  |  |  | 40694 |  | 39
211 | Modbus_K1_activation | DT_NUMERIC | M7692.7 | 40695 | R/W | 40
|  |  |  | 40696 |  | 41
|  |  |  | 40697 |  | 42
|  |  |  | 40698 |  | 43
|  |  |  | 40699 |  | 44
212 | Modbus_K2_activation | DT_NUMERIC | M7693.0 | 40700 | R/W | 45
|  |  |  | 40701 |  | 46
|  |  |  | 40702 |  | 47
|  |  |  | 40703 |  | 48
|  |  |  | 40704 |  | 49
|  |  |  | 40705 |  | 50
|  |  |  | 40706 |  | 51
|  |  |  | 40707 |  | 52
|  |  |  | 40708 |  | 53
|  |  |  | 40709 |  | 54
|  |  |  | 40710 |  | 55
|  |  |  | 40711 |  | 56
|  |  |  | 40712 |  | 57
|  |  |  | 40713 |  | 58
|  |  |  | 40714 |  | 59
|  |  |  | 40715 |  | 60
|  |  |  | 40716 |  | 61
|  |  |  | 40717 |  | 62
|  |  |  | 40718 |  | 63
|  |  |  | 40719 |  | 64
|  |  |  | 40720 |  | 65
213 | Battery_service_timer | DT_NUMERIC | MW2388 | 40721 | R | 66 | 24
|  |  |  | 40722 |  | 67
|  |  |  | 40723 |  | 68
|  |  |  | 40724 |  | 69
|  |  |  | 40725 |  | 70
|  |  |  | 40726 |  | 71
|  |  |  | 40727 |  | 72
|  |  |  | 40728 |  | 73
|  |  |  | 40729 |  | 74
|  |  |  | 40730 |  | 75
|  |  |  | 40731 |  | 76
|  |  |  | 40732 |  | 77
|  |  |  | 40733 |  | 78
|  |  |  | 40734 |  | 79
|  |  |  | 40735 |  | 80
|  |  |  | 40736 |  | 81
|  |  |  | 40737 |  | 82
|  |  |  | 40738 |  | 83
|  |  |  | 40739 |  | 84
|  |  |  | 40740 |  | 85
|  |  |  | 40741 |  | 86
|  |  |  | 40742 |  | 87
|  |  |  | 40743 |  | 88
|  |  |  | 40744 |  | 89
|  |  |  | 40745 |  | 90
214 | K1_output | DT_NUMERIC | M7693.2 | 40746 | R | 91 | #REF!